## Maintenance plan
WITKOP PREVENTATIVE MAINTENANCE PLAN 2023
Task No. | System | Equipment | Procedure Code | Title of Procedure | Task Description | No. of Equipment | Unit of measure | Frequency | Total Annual WL | WL Jan 23 | WL Feb 23 | WL Mar 23 | WL Apr 23 | WL May 23 | WL Jun 23 | WL Jul 23 | WL Aug 23 | WL Sep 23 | WL Oct 23 | WL Nov 23 | WL Dec 23
Astronergy CHSM6612P / SOLAR PV MODULES
1 | PV Array | Solar PV Modules | PM-001 | Biannualy Inspection to PV Modules. | 01. Revision Browning and Yellowing effect 02. Revision of possible damage on the surface of the panels. 03. Revision of Shadows on the panels and remove if necessary. 04. Visual revision of junction boxes. 05. Visual check of connectors and cables. 07. Visual check of stability, rigidity and fixing of the panels. | 99 | Trackers | 2 | 198 | 0 |  |  | 33 | 33 | 33 |  |  |  | 33 | 33 | 33
2 | PV Array | Solar PV Modules | PM-001 | Annualy Inspection to PV Modules. | 09. Thermography 10. Open circuit voltage measurement at string level. 11. Check the back sheets of panels for damage, mould, algae and delamination. 12. Visual check for inflammation, bubbling and/or non-uniformity of relief of the back sheet tedlar. | 99 | Trackers | 1 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0
3 | PV Array | Solar PV Modules | PM-001 | Annualy IV Curve test. | 13. IV Curve measurements of a sample of strings (25% where each string should be measured in a different row). | 108 | Combiner Box | 1 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0
4 | PV Array | Solar PV Modules | PM-001 | Annually Test in Laboratory. | 08. Laboratory flash test. | 10 | PV Module | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0
5 | PV Array | Solar PV Modules | PM-001 | Panel Cleaning to PV Modules. | 06. Panel cleaning. | 99 | Trackers | s | 99 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 99 | 0 | 0 | 0
Astronergy CHSM6612P / LOW VOLTAGE POWER LINES (DC and Grounding Network)
6 | 1 PV Array | Solar PV Modules | PM-002 | Biannually Visual inspection of string connections. | 03. Visual check of the MULTI-CONTACTs are in good condition. | 99 | Trackers | 2 | 198 | [5 empty] | 99 |  |  |  | 99
7 | 1 PV Array | Solar PV Modules | PM-002 | Annualy maintenance to cable strings. | 01. Check the condition pipelines and grounding of metal parts (trays). 02. Check the cabling supporting holders are in good condition. 04. Visual inspection of insulation, covering and splices. 05. Inspection of the critical points that appear in the electrical switchboards. 06. Inspection of the splices in the boxes where insulation faults usually occur. 07. Maintenance of the communication wiring. 08. Measurement of grounding resistance. | 99 | Trackers | 1 | 99 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0
Astronergy CHSM6612P / LOW VOLTAGE CHANNELING
8 | 1 PV Array | Low Voltage Channeling | PM-002.1 | Biannualy Channeling inspection. | 01. Metal tray: treating parts affected by corrosion and correct earth connection 02. PVC tray: treating sections that may be in bad state. 03. Tray channelling: inspection to avoid rodents. 03A. Check string cable guide wire is rigid and free of breakages and corrosion. | 99 | Trackers | 2 | 198 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 0
9 | 1 PV Array | Low Voltage Channeling | PM-002.1 | Annualy Channeling inspection. | 04. Buried channelling: verify sealing of tubes. | 99 | Trackers | 1 | 99 | 0 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kuadrotek / SECONDARY ELECTRICAL PANELS (Lever 1 Stream) String combiner box.
10 | 1 PV Array | String combiner box | PM-003 | SCADA strings control. | 20. Weekly Check for open strings (SCADA) | 99 | Tracker | 52 | 5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 PV Array | String combiner box | PM-003 | Quaterly Visual inspection for Combiner box structure. | 01. Checking for proper fastening, impacts, breaks or deformations of the Level 1 box. 05. Visual inspection of terminals, panels and conductors. 06. Visual inspection of pilots signals of fuses. 07. Grounding condition checking. | 99 | Trackers | 4 | 396 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
12 | 1 PV Array | String combiner box | PM-003 | Biannually Inspection for Combiner box. | 03. Check for proper sealing absence of humidity inside the box 04. Visual inspection of the enclosure associated components such as cable protectors, tightening screws, connectors, anchors. 08. Visual check for loose connections. 09. Location of switches and circuit breakers with deficiencies. 10. Check the condition of the surge arresters. 12. Visual check for possible overheating. 18. Circuit-breaker trip check. 19. Check the condition of the thermal magnet circuit-breakers. 21. Thermo graphical analysis of the electrical control panels 22. Electrical control panel voltages check. | 99 | Trackers | 2 | 198 |  |  |  | 33 | 33 | 33 |  |  | 33 | 33 | 33 | 0
13 | 1 PV Array | String combiner box | PM-003 | Annual Maintenance of Combiner box | 02. Electrical panels general clearing. 11. Insulation measurement of bus bars with respect to grounding. 13. Check the door and lock. 14. Check the plays and identify elements in the control panel and the electrical hazard identification plates. 15. Apply the contact cleaner to all the contacts in the switchboard. 16. Retightening of the screws. 17. Retightening of the switchboard's ring terminals. | 99 | Trackers | 1 | 99 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SunEdison AP90 / Tracker AP90
14 | PV Array | Trackers AP90 | PM-005 | Weekly SCADA Trackers monitoring. | 07. Monitor fault conditions. (SCADA). 07A. Check operating angels. (SCADA). | 99 | Trackers | 52 | 5148 | 396 | 396 | 495 | 396 | 396 | 495 | 396 | 495 | 396 | 396 | 495 | 396
15 | PV Array | Trackers AP90 | PM-005 | Quaterly Visual Inspection of Trackers. | 05. Structure torqued connections check. 06. Visually inspect system components for normal operation and alignment. 08. Tracker controller Inspection. 09. Inclinometer Inspection. 10. Anemometer Inspection. 11. Limit Switches Inspection, 12. Screw Jack Inspection and lubrication, 13. Steel Structure. | 99 | Trackers | 4 | 396 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
16 | PV Array | Trackers AP90 | PM-005 | Annual Maintenance of Trackers. | 01. Inspect module array for proper alignment and check a sample of module rail fasteners for proper connection. 02. Test wind slow function by triggering wind sensor. Repeat for snow and flood sensors if installed. 03. Inspect bearing housing assemblies for misalignment due to settling of piers and adjust position if necessary. 04. Inspect all electrical enclosures for cracking, pests and any other damage. | 99 | Trackers | 1 | 99 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0
ABB PVS800-57-0630kW / SOLAR PHOTOVOLTAIC - INVERTER
17 | CT Builing | Inverters PVS800-57-0630kW | PM-006 | Monthly Inspection of Inverters | 01. General inspection of the equipment. 02. Check the condition of cables and terminals. 05. Check the proper condition and operation of the lighting of the building replacing lamps or tubes if necessary. 11. Verify the absence of alarms in the control equipment. | 48 | Inverters | 12 | 576 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
18 | CT Builing | Inverters PVS800-57-0630kW | PM-006 | Quaterly Inspection of Inverters. | 03. Check the proper tightening of screws works and cables. 04. Visual check of connections. 08. Check the correct ventilation of the equipment. 09. Check the proper state of front air grate and rearwards filters. 13. Change batteries, when it's necessary. 14. Checking the grounding of the inverter. 15. Cleaning of inverter room. | 48 | Inverters | 4 | 192 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48
19 | CT Builing | Inverters PVS800-57-0630kW | PM-006 | Annual Maintenance of Inverters. | 06. Check the lack of humidity inside the cabinet. 07. Check the proper anchoring of equipment (upper and lower). 10. Check the environment condition. 12. Thermography: correct the detected hot spots. | 48 | Inverters | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0
Kuadrotek / SECONDARY ELECTRICAL PANELS (Lever 2 Stream) CC Cabinet.
20 | CT Builing | CC Cabinet | PM-004 | Monthly Inspection of CC Cabinet. | 20. Check the control panel lights and indicators. 23. Check the thermal magnetic device (negative, grounding isolation, monitoring and controller of inverter shutdown). 06. Visual inspection of pilots signals of fuses. | 48 | CC Cabinet | 52 | 2496 | 240 | 192 | 192 | 192 | 240 | 192 | 240 | 192 | 240 | 192 | 192 | 192
21 | CT Builing | CC Cabinet | PM-004 | Quaterly Inspection of CC Cabinet. | 01. Checking for proper fastening, impacts, breaks or deformations of the Level 2 box. 05. Visual inspection of terminals, panels and conductors. 07. Grounding condition checking.. | 48 | CC Cabinet | 4 | 192 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48
22 | CT Builing | CC Cabinet | PM-004 | Biannually Inspection of CC Cabinet. | 03. Checking for proper sealing, absence of humidity. 04. Visual inspection of the enclosure associated components such as cable protectors, tightening screws, connectors, anchors. 08. Visually check for possible loose connections. 09. Location of switches or circuit-breakers with possible deficiencies. 10. Checking the correct state of voltage dischargers. 12. Checking for possible excessive overheating of the busbar and the wiring. 18. Circuit-breaker trip check. 19. Inspection of the condition of the thermal magnetic circuit-breakers. 21. Thermo graphic analysis of the switchboard and correction of hot spots. 22. Checking the voltages of the switchboard. 24. Energy Meter Verification/Calibration. | 48 | CC Cabinet | 2 | 96 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0
23 | CT Builing | CC Cabinet | PM-004 | Annual Maintenance of CC Cabinet. | 02. Electrical panels general cleaning. 11. Insulation measurement of bus bars with respect to grounding. 13. Check the door and lock. 14. Check the good condition of the plates and identifying elements in the control panel and electrical hazard. identification plates are in good condition 15. Applying contact grease to all the contacts in the switchboard. 16. Re-tighten the panel protection device screws for the switchboard. 17. Re-tighten the panel ring terminals. | 48 | CC Cabinet | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0
PS / POWER TRANSFORMER (Dry)
24 | CT Builing | 22kV Power Transformer Dry. | PM-008 | Weekly Inspection of 22kV Power Transformer Dry, | 01A.Check Temperature 02A.Check Fans. 03A. Check status of SF6 gas on RMU. | 24 | Transformer | 52 | 1248 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
25 | CT Builing | 22kV Power Transformer Dry. | PM-008 | Quaterly Inspection of 22kV Power Transformer Dry. | 01. Check status of optical and acoustic indicators. 02. Check operation load level of measurement equipment. 03. Check ventilation operation. 04. Check winding temperature indicator (if available). 05. Check dielectric stiffness of power transformer. 06. Cleaning of room air filters. Replace if necessary. | 24 | Transformer | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
26 | CT Builing | 22kV Power Transformer Dry. | PM-008 | Annual Maintenance of 22kV Power Transformer Dry, | 07. Check status of current equipment for motor control 08. General review of operation of switchgear. 09. Openining and closing circuit breaker. 10. Opening and closing of switches manoeuvre. 11. Lubrication of the drive if necessary. 12. Inspection of terminal bottles. 13- Check the ground connections of the electrodes. 14. Wetting of ground wells. 15. Terminal and lid cleaning of power transformer. 16. Check Status of power transformer protection. 17. Check sealing of all joints of the power transformer. 18. Check the heating elements functioning of the power transformer. 19. Check air dryer (Replacement of silica gel when its colour is pink) of the power transformer. 20. Verification of electrical circuit breakers (SF6). 21. Verification of the mechanical circuit breakers status and operating of the circuit breaker interlocks. 22. Status and operating of the circuit breaker interlocks 23. Lubrication of circuit breakers. 24. Visual inspection of instrument transformer. 25. Press contact and review of instrument transformer connections. 26. Check condition of insulators and bus bars. 27. Check Status of insulators connections and bus bars. 28. Resistance measurement of ground network of neutral and hardware. 29. Protection relays checking. 30. Check alarm and trip signals of temperature. 31. Auxiliary relays checking. 32. Alarm system checking. 33. General cleaning. | 24 | Transformer | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0
PS / ARTIFICIAL VENTILATION
27 | CT Builing | Artifitial Ventilation | PM-009 | Weekly Inspection of Artifitial Ventilation. | 01. General state supervision. 02. Absence of unwanted noise checking. | 24 | Ventilation | 52 | 1248 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
28 | CT Builing | Artifitial Ventilation | PM-009 | Quaterly Inspection of Artifitial Ventilation. | 03. Exterior cleaning of equipment and components 04. Current measurement in phases. 05. Thermostat control checking and adjusting. 06. Check status of anchoring and vibration. 07. Check the room air filters and replace if is necessary. | 24 | Ventilation | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
PS / MEDIUM VOLTAGE POWER LINES (AC and Grounding Network)
29 | CT Builing | MV Power line and grounding network. | PM-010 | Annual Inspection of MV Power lind and Grounding network. | 01. Check the condition pipelines and grounding of metal parts (trays). 02. Check the holder condition. 03. Check absence of heating's or vibrations 04. General check of grounding lines. 05. Check the contact and pass heating. 06. Measurement of grounding resistance. | 24 | CT Building | 1 | 24 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0
CONTROL AND SYSTEMS / COMMUNICATIONS
30 | SCADA | Communication systems | PM-011 | Monthly Inspection Communication System | 01. General functioning status checking. | 1 | COMMS | 52 | 52 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
31 | SCADA | Communication systems | PM-011 | Quaterly Inspection of Communication System | 02. Checking of external connections. 03. Exterior cleaning | 1 | COMMS | 4 | 4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
CONTROL AND SYSTEMS / SCADA CONTROL
32 | SCADA | SCADA monitoring | PM-012 | Daily monitoring of SCADA | 01. General functioning status checking. | 1 | SCADA | 365 | 365 | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
33 | SCADA | SCADA monitoring | PM-012 | Quaterly Inspection of SCADA System | 02. External connection checking and retightening 03. Exterior cleaning | 1 | SCADA | 4 | 4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
34 | SCADA | SCADA monitoring | PM-012 | Back up of SCADA | 04. Backups (software and data) | 1 | SCADA | s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GEONICA 3000C / CR1000 WEATHER STATION
35 | MDAS | MET Station | PM-013 | Weekly Inspection of MDAS | 01. General cleaning and inspection of all elements and meteorological sensors. 02. Check of dirt condition of the panels. 12. Cleaning irradiance cells and/or pyranometes with damp cloth and deionised water and keep log book. | 4 | MDAS | 52 | 208 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
36 | MDAS | MET Station | PM-013 | Biannual Inspection of MDAS | 03. Weather temperature measurement and comparison with weather station. 04. Inspection of element anchoring and bolt fastenings. 05. Inspection of verticality and anchoring of mast. | 4 | MDAS | 4 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0
37 | MDAS | MET Station | PM-013 | Annual Maintenance of MDAS | 06. Maintenance of earth systems. 07. Maintenance of electrical installation. 08. Review lightning conductor installation. 10. Check the condition of the supports for the sensors. | 4 | MDAS | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0
38 | MDAS | MET Station | PM-013 | Calibration and Check of MDAS | 09. Review and replace desiccant according to manufacturer instructions. 11. Calibration of pyranometer/reference cell (according to manufacturer instructions) at an official institute. | 4 | MDAS | s | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PS-LV_AUX_FV / SECONDARY ELECTRICAL PANELS (Consumption) Energy Meter cabinet.
39 | CT Builing | Energy Meter Cabinet | PM-014 | Monthly Inspection of Energy Meter | 06. Visual inspection of pilots signals of fuses. 20. Checking the panel lights and indicators. | 24 | CT Building | 52 | 1248 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
40 | CT Builing | Energy Meter Cabinet | PM-014 | Quaterly Inspection of Energy Meter | 01. Checking for proper fastening, possible impacts, breaks or deformations. 05. Visual inspection of terminals, panels and conductors. 07. Grounding condition checking. | 24 | CT Building | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
41 | CT Builing | Energy Meter Cabinet | PM-014 | Biannual Inspection of Energy Meter | 03. Checking for proper sealing, absence of humidity. 04. Visual inspection of the enclosure. 08. Visually check for possible loose connections. 09. Location of switches or circuit-breakers with possible deficiencies. 10. Checking the correct state of voltage dischargers. 12. Checking for possible excessive overheating. 18. Circuit-breaker trip check. 19. Inspection of the condition of the thermal magnetic circuit-breakers. 21. Thermographic analysis of the switchboard. 22. Checking the voltages of the switchboard. 23. Energy Meters Calibration. | 24 | CT Building | 2 | 48 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24
42 | CT Builing | Energy Meter Cabinet | PM-014 | Annual Maintenance of Energy Meter. | 02. Electrical panels general clearing 11. Insulation measurement of bus bars with respect to grounding. 13. Check the door and lock. 14. Check the good condition of the plates and identifying elements in the control panel. 15. Applying contact cleaner. 16. Re-tighten the panel protection device screws. 17. Re-tighten the panel ring terminals. | 24 | CT Building | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0
SECURITY SYSTEM / MANUAL FIRE ALARM SYSTEM
43 | General | Security System & Fire Alarm | PM-015 | Quaterly Inspection to Security and fire alarm systems. | 01. Condition checking of emergency battery. 02. Performance checking of alarm devices. 08. Check location, accessibility and visibility of fire extinguishers. | 24 | CT Building | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
44 | General | Security System & Fire Alarm | PM-015 | Test Check for Security and Fire alarm systems. | 03. Inspection of operation of installations (with each power source). Each 4 months. | 24 | CT Building | 3 | 72 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24
45 | General | Safety System & Fire Alarm | PM-015 | Annual Maintenance of Security and fire alarm systems. | 04. Checking of the overall performance of the installation 05. Cleaning of the components 06. Manual extinguishers revision: - Check the place they are located, accessibility and visibility - Check the correct status of the seals and that they have not been used - External aspect: Absence of corrosion and impacts) - Check the proper pressure indication on the manometer 07. Final test setup (with each power source). | 24 | CT Building | 1 | 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0
GENERATOR / POWER GENERATOR
46 | General | Power Generator | PM-016 | Monthly Inspection of Generator Auxliliary. | 01. General status checking. | 1 | Generator | 12 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
47 | General | Power Generator | PM-016 | Bi-Monthly check of Generator (Fornightly). | 02. Start-up batteries connection checking. 03. Grease pump operation checking. 04. Checking of oil, air and fuel levels. 05. Network failure simulation. 06. Checking of automatic start-up of power generator. 07. Checking of automatic performance of network switches and power generator. 08. Checking of power generator's automatic stop. | 1 | Generator | 6 | 6 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1
48 | General | Power Generator | PM-016 | Biannually Inspection of Generator. | 09. Exterior cleaning 10. Brushes and collectors cleaning and condition checking 11. Engine protection alarms checking 12.Unwanted noise and vibration checking | 1 | Generator | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
49 | General | Power Generator | PM-016 | Anual Maintenance of Generator. | 13. Replacement of alternator engine oil (three years). 14. Replacement oil, air and fuel filters (500 hours or 30 months). 15. Replacement of start-up batteries (3 years). | 1 | Generator | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Security System / CCTV.
50 | General | Security System CCTV | PM-017 | Biannually Maintenance of CCTV System. | 01. Checking of all local functions of the Commander, (UP, DOWN, ZOOM, FOCUS), as well as the bumpers of petitioners 02. Check the definition and signal levels from the camera 03. Checking of all feeding stabilised power sources (Amplification systems, camera tensions, systems) 04. Observation of status indicators for the electronic centre 05. General testing of electronic centre system, adjusting timers. 06. Checking of voltage at terminals connected to the detectors of the electronic centre. 07. Checking of performance indicators and testing of expansion PV modules 08. Checking the state and correct functioning of the microwave/infrared barriers 09. Checking the voltage and level of charge of the central control unit batteries. | 45 | Cameras | 1 | 45 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0
51 | General | Security System CCTV | PM-017 | Annually Inspection of CCTV System. | 10. Checking the value of the supply voltage for all the equipment and elements that make up the security installation. 11. Checking the condition of the supports, towers or columns. | 45 | Cameras | 2 | 90 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FENCES / HARDWARE (Perimeter Fence and Accesses)
52 | General | Perimeter Fence | PM-018 | Inspection of the Perimeter Fence. - Each 4 months. | 08. Maintenance of good condition of water drainage system, cleaning and civil maintenance works. 09. Inspect all manholes to ensure that they are intact and that excessive sand or water is not entering them. | 45 | Cameras | 3 | 135 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 45
53 | General | Perimeter Fence | PM-018 | Biannual Maintenance of Perimeter Fence. | 01. Status checking of perimeter fence. 02. Status checking of access gates. 03. Functioning status of latches and hinges 04. Lubrication of gates. 05. Checking of fence corrosion status, proceeding to paint if necessary. 06. Status checking of vegetation, removing if necessary. 07. Apply herbicides in areas of fencing. 10. Maintenance of good condition in internal and access roads. | 45 | Cameras | 2 | 90 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 45 | 0
CIVIL WORKS / CLEARING AND PEST CONTROL
54 | General | All Site | PM-019 | Monthly Visual Inspection Clearing and Pest Control. | 01. General status checking. 05. Visual inspection of inverters buildings for signs of rodents. | 24 | CT Building | 12 | 288 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
55 | General | All Site | PM-019 | Pest Control Application. | 04. Treatment of pest control. Each 4 months. | 24 | CT Building | 3 | 72 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0
56 | General | All Site | PM-019 | Biannually Chemical Control | 02. Chemical weed control / Physical removal as appropriate / grass-cutting. 03. Clearing of small plants that have withstood the chemical treatment. | 99 | CT Building | 2 | 198 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0
SUBSTATION / SUBSTATION - CONTROL BUILDING
57 | Substation | Substation | PM-020 | Monthly Inspection of Substation. | 01.Check Feeder one B/B 132kv Isolator if the links are Closed and locked in all phases 02.Check Feeder One 132kv CT's if Rph,Wph,Bph oil level is correct 03.Check TRFR One 132Kv Breaker is Closed,SF6-Gas Normal and the Counter 04.Check TRFR One 132Kv CT's if Rph,Wph,Bph oil level is correct 05.TRFR One 132Kv Isolator if the links are Closed and locked in all phases,Earth link open B/B side, Earth link open TRFR side 06.TRFR One 132Kv VT's if Rph,Wph,Bph oil level is correct and all CB's Switched on. 07.Transfomer 1 & 2 -Check if main oil level is correct -Check if bucholtz Not Operated -Check if the explosion device not operated -Check if HV surge Arrestors are in order -Check if MV Surge Arrestor are in order -Check oil temperature -Check winding Temperature -Check Ambient Temperature -Check if kiosk is on -Check if Heater is on -Check if silica Gel not coloured -Check if oil level is Correct -Check if main oil level is correct -Check tap changer -Check if the heater is on -Check if the light is on -Check tap changer -Check silica Gel not Coloured -Check earth counter 08. Transformer 1&2 NEC/NER -Check if main oil level is correct -Check if bucholtz Not Operated -Check if the explosion device not operated -Check oil temperature -Check winding Temperature -Check silica Gel not Coloured -Check 22kv Cable in Good condition | 2 | Trasnformer | 12 | 24 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
37 | Substation | Substation | PM-020 | Mantenimiento del Sistema de Iluminacion | Mantenimiento del Sistema de Iluminacion cambiando luces en mal estado. | 1 | Unidad | 1 | 1 | [7 empty] | 1
58 | Substation | Substation | PM-020 | Major Maintenance of Substation. | 01. Cleaning of control panel. 02. Review of operation of signal lamps on the control panel. 03. Function Testing relay of control panel. 04. Test cuts from the relay control panel. 05. Checking of the operation of electromechanical relays on the control panel 06. Review and tighten of terminals at the control panel 07. Manoeuvres making with control panel remote controls 08. Review of operation of automatic and differential Auxiliary Service 09. Review of operation of the remote control and lamp signalling on control panel and auxiliary services 10. Review and tighten the terminals of the Auxiliary Service 11. Review DC battery 12. Check of the high-voltage safety 13. Fire protection material testing 14. Regular lighting testing 15. Emergency lighting testing | 1 | Substation | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
SUBSTATION / SUBSTATION - SUBSTATION CELLS
59 | Substation | Substation Cells | PM-021 | Biannually Inspection of Substation Cells. | 01. Envelope status check 02. Inspection and if necessary retightening of bolts 03. Checking the state of bus bars 04. Interior Cleaning of the cell, bus bars and insulators 05. Cable and terminal bottles checking 06. Check operation of heating element 07. Checking of fuses, auxiliary relays and signal lamp 08. Checking the status of mechanical interlocks 09. Review of mechanical interlocking of cells 10. Joint manoeuvring of the interlocking 11. Checking of manoeuvre signalling on control panel 12. Checking of power cut mechanism 13. General cleaning and lubrication of moving parts | 2 | Transformer | 2 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
SUBSTATION / SUBSTATION - AUXILIARY SERVICE POWER TRANSFORMER
60 | Substation | AASS Power Transformer | PM-023 | Annual Maintenance of Auxiliary Power Transformers. | 01. Check general condition. 02. Inspection and if necessary retightening of bolts. 03. Check operation of temperature sensors. 04. Current measurements in high and low voltage. 05. Checking the state of the cables and terminal bottles.. 06. Ground resistance measurement. 07. Inspection and tightening if necessary of terminal. 08. Measurement of dielectric strength of oil (every 5 years). 09. General Cleaning (see 10.1.1 and (see 10.1.2)). 10. Control encapsulated insulation (see 10.1.7). 11. Control the value of compression of supports (see 10.1.8). 12. Humidity, thermo resistance and functionality control (see 10.1.4, 10.1.5, 10.1.6). 13. General cleaning and lubrication of moving parts. | 2 | Transformer | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
SUBSTATION / SUBSTATION - MV/HV POWER TRANSFORMER
61 | Substation | MV-HV Power Transformer | PM-024 | Major Maintenance of MV-HV Transformers. | 01. Check general condition. 02. Inspection and if necessary retightening of bolts. 03. Check operation of temperature sensors. 04. Current measurements in high and low voltage. 05. Checking the state of the cables and terminal bottles. 06. Ground resistance measurement. 07. Inspection and tightening if necessary of terminals. 08. Measurement of dielectric strength of oil (every 5 years). 09. General Cleaning. 10. Control encapsulated insulation. 11. Control the value of compression of supports. 12. Humidity, thermoresistence and functionality control. | 2 | Transformer | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
O&M Building and Facilities
62 | O&M Facilities | Buildings and Internal roads | PM-025 | Monthly Inspection of O&M building and Internal roads. | 01. Check general condition of O&M buildings 02. Inspection and if necessary repair any defects 03. Check condition of internal roads 04. Inspect storage areas | 1 | Facilities | 12 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Jan-Dec 2026
2026 | January
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2025-12-29 | 2025-12-30 | 2025-12-31 | 2026-01-01 | 2026-01-02 | 2026-01-03 | 2026-01-04
|  |  | Public holiday | PM-009 Weekly Artifitial Ventilation
LEGEND
2026-01-05 | 2026-01-06 | 2026-01-07 | 2026-01-08 | 2026-01-09 | 2026-01-10 | 2026-01-11
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-003 Annual Maintenance of Combiner box | PM-020 Monthly Inspection of Substation. | PM-009 Weekly Artifitial Ventilation |  |  |  |  | WEEKLY
PM-003 SCADA strings control. |  | PM-003 Quaterly Visual inspection for Combiner box structure. | PM-016 Bi-Monthly check of Generator (Fortight). | [5 empty] | MONTHLY
QUARTERLY
2026-01-12 | 2026-01-13 | 2026-01-14 | 2026-01-15 | 2026-01-16 | 2026-01-17 | 2026-01-18 |  |  | BI-ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM-025 Monthly Inspection of O&M building and Internal roads. | PM-009 Weekly Artifitial Ventilation |  |  |  |  | ANNUAL
| PM-003 SCADA strings control. | [7 empty] | PUBLIC HOLIDAY
BI-MONTHLY
2026-01-19 | 2026-01-20 | 2026-01-21 | 2026-01-22 | 2026-01-23 | 2026-01-24 | 2026-01-25
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-016 Monthly Inspection of Generator Auxliliary. | PM-008 Monthly Inspection of 22kV Power Transformer Dry, | PM 006 - Monthly Inspection of Inverters
| PM-003 SCADA strings control. |  | PM-009 Artifitial Ventilation | PM 004 - Monthly Inspection of CC Cabinet. Done
PM 014 - Monthly Inspection of Energy Meter
2026-01-26 | 2026-01-27 | 2026-01-28 | 2026-01-29 | 2026-01-30 | 2026-01-31 | 2026-02-01
PM 013 - Weekly Inspection of Weather Stations | PM-016 Bi-Monthly check of Generator (Fortight). | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation
Complete Outstanding PM's and reports | PM-005 - Weekly SCADA Trackers monitoring.
PM-003 SCADA strings control.
2026 | February
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-01-26 | 2026-01-27 | 2026-01-28 | 2026-01-29 | 2026-01-30 | 2026-01-31 | 2026-02-01
2026-02-02 | 2026-02-03 | 2026-02-04 | 2026-02-05 | 2026-02-06 | 2026-02-07 | 2026-02-08
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation |  |  |  |  | LEGEND
PM-003 SCADA strings control. | PM-020 Monthly Inspection of Substation.
2026-02-09 | 2026-02-10 | 2026-02-11 | 2026-02-12 | 2026-02-13 | 2026-02-14 | 2026-02-15 |  |  | WEEKLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation |  |  |  |  | MONTHLY
PM-003 SCADA strings control. |  |  | PM-016 Bi-Monthly check of Generator (Fortight). | [5 empty] | QUARTERLY
2026-02-16 | 2026-02-17 | 2026-02-18 | 2026-02-19 | 2026-02-20 | 2026-02-21 | 2026-02-22 |  |  | BI-ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-025 Monthly Inspection of O&M building and Internal roads. | PM 006 - Monthly Inspection of Inverters | PM-008 Monthly Inspection of 22kV Power Transformer Dry, |  |  |  |  | ANNUAL
PM-003 SCADA strings control. | PM-016 Monthly Inspection of Generator Auxliliary. |  | PM 004 - Monthly Inspection of CC Cabinet. Done | PM-009 Weekly Artifitial Ventilation |  |  |  |  | PUBLIC HOLIDAY
|  |  | PM 014 - Monthly Inspection of Energy Meter | [5 empty] | BI-MONTHLY
2026-02-23 | 2026-02-24 | 2026-02-25 | 2026-02-26 | 2026-02-27 | 2026-02-28 | 2026-03-01
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM-016 Bi-Monthly check of Generator (Fortight). | PM-009 Weekly Artifitial Ventilation
PM-003 SCADA strings control.
2026 | March
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-02-23 | 2026-02-24 | 2026-02-25 | 2026-02-26 | 2026-02-27 | 2026-02-28 | 2026-03-01
2026-03-02 | 2026-03-03 | 2026-03-04 | 2026-03-05 | 2026-03-06 | 2026-03-07 | 2026-03-08
PM 013 - Weekly Inspection of Weather Stations | PM-020 Monthly Inspection of Substation. | PM 005 - Quaterly Visual Inspection of Trackers. | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation | [5 empty] | LEGEND
PM-003 SCADA strings control. | PM-005 - Weekly SCADA Trackers monitoring.
2026-03-09 | 2026-03-10 | 2026-03-11 | 2026-03-12 | 2026-03-13 | 2026-03-14 | 2026-03-15 |  |  |  | WEEKLY
PM 013 - Quaterly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM 012 - Quaterly Inspection of SCADA System done | 013 - Calibration and Check of MDAS | PM-008 Quaterly Inspection of 22kV Power Transformer Dry, | [5 empty] | MONTHLY
PM-003 SCADA strings control. |  | PM-016 Bi-Monthly check of Generator (Fortight). | PM 006 - Quaterly Inspection of Inverters | PM-009 Quaterly Artifitial Ventilation | [5 empty] | QUARTERLY
|  |  | PM 004 - Quaterly Inspection of CC Cabinet. Done | [6 empty] | BI-ANNUAL
2026-03-16 | 2026-03-17 | 2026-03-18 | 2026-03-19 | 2026-03-20 | 2026-03-21 | 2026-03-22 |  |  |  | ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM 013 - Weekly Inspection of Weather Stations | PM-016 Quaterly Inspection of Generator Auxliliary. | PM-009 Artifitial Ventilation | Public Holiday | Public Holiday |  |  |  |  | PUBLIC HOLIDAY
PM-003 SCADA strings control. | PM-003 SCADA strings control. | PM-016 Anual Maintenance of Generator. | PM 014 - Quaterly Inspection of Energy Meter | [6 empty] | BI-MONTHLY
2026-03-23 | 2026-03-24 | 2026-03-25 | 2026-03-26 | 2026-03-27 | 2026-03-28 | 2026-03-29
PM 013 - Weekly Inspection of Weather Stations | PM 015 - Quaterly Inspection to Security and fire alarm systems. | PM-025 Quaterly Inspection of O&M building and Internal roads. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports
PM-003 SCADA strings control. | PM 011 - Quaterly Inspection of Communication System |  | PM-016 Bi-Monthly check of Generator (Fortight).
PM-005 - Weekly SCADA Trackers monitoring.
2026 | April
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-03-30 | 2026-03-31 | 2026-04-01 | 2026-04-02 | 2026-04-03 | 2026-04-04 | 2026-04-05
Complete Outstanding PM's and reports | PM-005 - Weekly SCADA Trackers monitoring. | PM-002.1 Biannualy Channeling inspection. | PM-020 Monthly Inspection of Substation. | Public Holiday |  | Public Holiday
| PM 013 - Weekly Inspection of Weather Stations |  | PM-009 Weekly Artifitial Ventilation
| PM-003 SCADA strings control. |  | PM-016 Bi-Monthly check of Generator (Fortight).
2026-04-06 | 2026-04-07 | 2026-04-08 | 2026-04-09 | 2026-04-10 | 2026-04-11 | 2026-04-12
Public Holiday | PM-005 - Weekly SCADA Trackers monitoring. | PM-003 Biannually Inspection for Combiner box. | PM-017 Annually Inspection of CCTV System. | PM-009 Weekly Artifitial Ventilation |  |  |  |  | LEGEND
PM-003 SCADA strings control. | PM 013 - Weekly Inspection of Weather Stations | PM-003 SCADA strings control.
2026-04-13 | 2026-04-14 | 2026-04-15 | 2026-04-16 | 2026-04-17 | 2026-04-18 | 2026-04-19 |  |  | WEEKLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-001 Biannualy inspectiom of PV Modules | PM 005 - Annual Maintenance of Trackers. | [5 empty] | MONTHLY
PM-003 SCADA strings control. |  |  | PM-009 Artifitial Ventilation | [5 empty] | QUARTERLY
2026-04-20 | 2026-04-21 | 2026-04-22 | 2026-04-23 | 2026-04-24 | 2026-04-25 | 2026-04-26 |  |  | BI-ANNUAL
PM-003 SCADA strings control. | PM-005 - Weekly SCADA Trackers monitoring. | PM-018 Biannual Inspection of the Perimeter Fence | PM 006 - Monthly Inspection of Inverters | PM-008 Monthly Inspection of 22kV Power Transformer Dry, |  |  |  |  | ANNUAL
PM 013 - Weekly Inspection of Weather Stations |  | PM-016 Monthly Inspection of Generator Auxliliary. | PM 004 - Monthly Inspection of CC Cabinet. Done | PM-009 Weekly Artifitial Ventilation |  |  |  |  | PUBLIC HOLIDAY
|  | PM-025 Monthly Inspection of O&M building and Internal roads. | PM 014 - Monthly Inspection of Energy Meter | PM-016 Bi-Monthly check of Generator (Fortight). |  |  |  |  | BI-MONTHLY
2026-04-27 | 2026-04-28 | 2026-04-29 | 2026-04-30 | 2026-05-01 | 2026-05-02 | 2026-05-03
Public holiday | PM-005 - Weekly SCADA Trackers monitoring. | PM-003 SCADA strings control.
PM 013 - Weekly Inspection of Weather Stations
2026 | May
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-04-27 | 2026-04-28 | 2026-04-29 | 2026-04-30 | 2026-05-01 | 2026-05-02 | 2026-05-03
Public holiday |  | PM-020 Monthly Inspection of Substation. |  | Public holiday
|  | Panel Cleaning to PV Modules | PM-009 Weekly Artifitial Ventilation
2026-05-04 | 2026-05-05 | 2026-05-06 | 2026-05-07 | 2026-05-08 | 2026-05-09 | 2026-05-10
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-001 Biannualy inspectiom of PV Modules | PM-002.1 Biannualy Channeling inspection | PM-009 Weekly Artifitial Ventilation |  | Public holiday |  |  | LEGEND
PM-003 SCADA strings control. |  |  |  | PM-016 Bi-Monthly check of Generator (Fortight).
2026-05-11 | 2026-05-12 | 2026-05-13 | 2026-05-14 | 2026-05-15 | 2026-05-16 | 2026-05-17 |  |  | WEEKLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-003 Biannually Inspection of Combiner box. | PM 005 - Annual Maintenance of Trackers. | PM-009 Weekly Artifitial Ventilation |  |  |  |  | MONTHLY
PM-003 SCADA strings control. |  |  | PM-002 Annualy maintenance to cable strings. | [5 empty] | QUARTERLY
2026-05-18 | 2026-05-19 | 2026-05-20 | 2026-05-21 | 2026-05-22 | 2026-05-23 | 2026-05-24 |  |  | BI-ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-025 Monthly Inspection of O&M building and Internal roads. | PM-016 Monthly Inspection of Generator Auxliliary. | PM-009 Weekly Artifitial Ventilation |  |  |  |  | ANNUAL
PM-003 SCADA strings control. |  |  |  | PM-016 Bi-Monthly check of Generator (Fortight). |  |  |  |  | PUBLIC HOLIDAY
2026-05-25 | 2026-05-26 | 2026-05-27 | 2026-05-28 | 2026-05-29 | 2026-05-30 | 2026-05-31 |  |  | BI-MONTHLY
|  | PM 006 - Monthly Inspection of Inverters | PM-008 Montly Inspection of 22kV Power Transformer Dry, | Complete Outstanding PM's and reports
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM 004 - Monthly Inspection of CC Cabinet. Done
PM-003 SCADA strings control. |  | PM 014 - Monthly Inspection of Energy Meter
2026 | June
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-06-01 | 2026-06-02 | 2026-06-03 | 2026-06-04 | 2026-06-05 | 2026-06-06 | 2026-06-07
2026-06-08 | 2026-06-09 | 2026-06-10 | 2026-06-11 | 2026-06-12 | 2026-06-13 | 2026-06-14
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM 005 - Annual Maintenance of Trackers. | PM-002 Annualy maintenance to cable strings. | PM-009 Weekly Artifitial Ventilation |  |  |  | LEGEND
PM-003 SCADA strings control. | PM-020 Monthly Inspection of Substation. | PM 011 - Quaterly Inspection of Communication System | 001 Biannualy inspectiom to PV Modules
Tractor Service, Brush Cutters & Ride-on |  |  | PM-003 Biannually Inspection for Combiner box. |  |  |  |  | WEEKLY
2026-06-15 | 2026-06-16 | 2026-06-17 | 2026-06-18 | 2026-06-19 | 2026-06-20 | 2026-06-21 |  | MONTHLY
PM 013 - Quaterly Inspection of Weather Stations |  | PM 005 - Quaterly Visual Inspection of Trackers. | Complete Outstanding PM's and reports | PM-008 Quaterly Inspection of 22kV Power Transformer Dry, |  | Public holiday |  | QUARTERLY
PM-003 SCADA strings control. | Public holiday | PM-005 - Weekly SCADA Trackers monitoring. | PM-016 Bi-Monthly check of Generator (Fortight). | PM-009 Quaterly Inspection of Artifitial Ventilation |  |  |  | BI-ANNUAL
2026-06-22 | 2026-06-23 | 2026-06-24 | 2026-06-25 | 2026-06-26 | 2026-06-27 | 2026-06-28 |  | ANNUAL
| PM-005 - Weekly SCADA Trackers monitoring. | PM 015 - Quaterly Inspection to Security and fire alarm systems. | PM-025 Quaterly Inspection of O&M building and Internal roads. | PM-009 Weekly Artifitial Ventilation |  |  |  | PUBLIC HOLIDAY
| PM 013 - Weekly Inspection of Weather Stations | PM 012 - Quaterly Inspection of SCADA System done | [5 empty] | BI-MONTHLY
2026-06-29 | 2026-06-30 | 2026-07-01 | 2026-07-02 | 2026-07-03 | 2026-07-04 | 2026-07-05
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM 006 - Quaterly Inspection of Inverters | PM-009 Weekly Artifitial Ventilation
PM-003 SCADA strings control. |  | PM-016 Bi-Monthly check of Generator (Fortight). | PM 004 - Quaterly Inspection of CC Cabinet. Done
PM 014 - Biannual Inspection of Energy Meter
2026-07-06 | 2026-07-07 | Notes:
2026 | July
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-06-29 | 2026-06-30 | 2026-07-01 | 2026-07-02 | 2026-07-03 | 2026-07-04 | 2026-07-05
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-020 Monthly Inspection of Substation. | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation
PM-003 SCADA strings control. |  | PM 011 - Monthly Inspection Communication System
2026-07-06 | 2026-07-07 | 2026-07-08 | 2026-07-09 | 2026-07-10 | 2026-07-11 | 2026-07-12
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM-002 Annualy maintenance to cable strings. | PM-009 Weekly Artifitial Ventilation |  |  |  | LEGEND
PM-003 SCADA strings control. |  |  | PM-016 Bi-Monthly check of Generator (Fortight).
2026-07-13 | 2026-07-14 | 2026-07-15 | 2026-07-16 | 2026-07-17 | 2026-07-18 | 2026-07-19 |  | WEEKLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-016 Monthly Inspection of Generator Auxliliary. | Public holiday | PM-009 Weekly Artifitial Ventilation | Public holiday |  |  | MONTHLY
PM-003 SCADA strings control. |  | PM-025 Monthly Inspection of O&M building and Internal roads. | [5 empty] | QUARTERLY
2026-07-20 | 2026-07-21 | 2026-07-22 | 2026-07-23 | 2026-07-24 | 2026-07-25 | 2026-07-26 |  | BI-ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM 006 - Monthly Inspection of Inverters | PM-008 Monthly Inspection of 22kV Power Transformer Dry, |  |  |  | ANNUAL
PM-003 SCADA strings control. |  | PM-016 Bi-Monthly check of Generator (Fortight). | PM 004 - Monthly Inspection of CC Cabinet. Done | PM-009 Weekly Artifitial Ventilation |  |  |  | PUBLIC HOLIDAY
2026-07-27 | 2026-07-28 | 2026-07-29 | 2026-07-30 | 2026-07-31 | 2026-08-01 | 2026-08-02 |  | BI-MONTHLY
Complete Outstanding PM's and reports | PM 014 - Monthly Inspection of Energy Meter | Complete Outstanding PM's and reports
2026 | August
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-07-27 | 2026-07-28 | 2026-07-29 | 2026-07-30 | 2026-07-31 | 2026-08-01 | 2026-08-02
|  |  | PM-020 Monthly Inspection of Substation. | PM-008 Quaterly Inspection of 22kV Power Transformer Dry,
|  |  | PM-003 Quaterly Visual inspection for Combiner box structure. | PM-009 Quaterly inspection of Artifitial Ventilation
2026-08-03 | 2026-08-04 | 2026-08-05 | 2026-08-06 | 2026-08-07 | 2026-08-08 | 2026-08-09
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-020 Monthly Inspection of Substation. | PM-009 Weekly Artifitial Ventilation |  |  | Public holiday |  | LEGEND
PM-003 SCADA strings control. | Calibration of tools | PM 011 - Monthly Inspection Communication System
2026-08-10 | 2026-08-11 | 2026-08-12 | 2026-08-13 | 2026-08-14 | 2026-08-15 | 2026-08-16 |  | WEEKLY
Public holiday | PM-005 - Weekly SCADA Trackers monitoring. | PM 012 - Quaterly Inspection of SCADA System | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation |  |  |  | MONTHLY
| PM 013 - Annual Maintenance of MDAS |  | PM-016 Bi-Monthly check of Generator (Fortight). |  |  |  |  | QUARTERLY
2026-08-17 | 2026-08-18 | 2026-08-19 | 2026-08-20 | 2026-08-21 | 2026-08-22 | 2026-08-23 |  | BI-ANNUAL
PM 013 - Quaterly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-016 Monthly Inspection of Generator Auxliliary. | PM-018 Inspection of the Perimeter Fence. - Each 4 months. | PM-008 Monthly Inspection of 22kV Power Transformer Dry, |  |  |  | ANNUAL
PM-003 SCADA strings control. | PM 005 - Quaterly Visual Inspection of Trackers. | PM-025 Monthly Inspection of O&M building and Internal roads. |  | PM-009 Weekly Artifitial Ventilation |  |  |  | PUBLIC HOLIDAY
2026-08-24 | 2026-08-25 | 2026-08-26 | 2026-08-27 | 2026-08-28 | 2026-08-29 | 2026-08-30 |  | BI-MONTHLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM 006 - Quaterly Inspection of Inverters | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports
PM-003 SCADA strings control. | PM 014 - Monthly Inspection of Energy Meter | PM 004 - Quaterly Inspection of CC Cabinet. Done | PM-016 Bi-Monthly check of Generator (Fortight).
2026 | September
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-08-31 | 2026-09-01 | 2026-09-02 | 2026-09-03 | 2026-09-04 | 2026-09-05 | 2026-09-06
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-020 Major Maintenance of Substation. | Complete Outstanding PM's and reports | PM-009 Weekly Artifitial Ventilation
PM-003 SCADA strings control.
2026-09-07 | 2026-09-08 | 2026-09-09 | 2026-09-10 | 2026-09-11 | 2026-09-12 | 2026-09-13
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-003 Biannually Inspection for Combiner box. | PM 010 - Annual Inspection of MV Power line and Grounding network. | PM-009 Weekly Artifitial Ventilation
PM-003 SCADA strings control. | PM 015 - Annual Maintenance of Security and fire alarm systems. |  | PM-016 Bi-Monthly check of Generator (Fortight). |  |  |  |  | LEGEND
2026-09-14 | 2026-09-15 | 2026-09-16 | 2026-09-17 | 2026-09-18 | 2026-09-19 | 2026-09-20
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM 008 - Annual Maintenance of 22kV Power Transformer Dry |  |  |  | WEEKLY
PM-003 SCADA strings control. |  |  |  | PM-009 Weekly Artifitial Ventilation |  |  |  | MONTHLY
2026-09-21 | 2026-09-22 | 2026-09-23 | 2026-09-24 | 2026-09-25 | 2026-09-26 | 2026-09-27 |  | QUARTERLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-016 Bi-Monthly check of Generator (Fortight). | Public holiday | PM-009 Weekly Artifitial Ventilation |  |  |  | BI-ANNUAL
PM-003 SCADA strings control. | [7 empty] | ANNUAL
2026-09-28 | 2026-09-29 | 2026-09-30 | 2026-10-01 | 2026-10-02 | 2026-10-03 | 2026-10-04 |  | PUBLIC HOLIDAY
BI-MONTHLY
2026 | October
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-09-28 | 2026-09-29 | 2026-09-30 | 2026-10-01 | 2026-10-02 | 2026-10-03 | 2026-10-04
PM-005 - Weekly SCADA Trackers monitoring. | PM-005 - Weekly SCADA Trackers monitoring. | PM 006 - Annual Maintenance of Inverters. | M 014 - Annual Maintenance of Energy Meter. | PM-009 Weekly Artifitial Ventilation
PM 013 - Weekly Inspection of Weather Stations | PM-020 Monthly Inspection of Substation. | PM 004 - Annual Inspection of CC Cabinet. Done
PM-003 SCADA strings control.
2026-10-05 | 2026-10-06 | 2026-10-07 | 2026-10-08 | 2026-10-09 | 2026-10-10 | 2026-10-11
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-001 Panel Cleaning to PV Modules. | PM-003 Biannually Inspection for Combiner box. | PM-009 Artifitial Ventilation |  |  |  | LEGEND
PM-003 SCADA strings control. | PM-001 Annualy Inspection to PV Modules. | PM-001 Biannualy inspectiom to PV Modules | PM-002 Biannually Visual inspection of string connections. | PM-016 Bi-Monthly check of Generator (Fortight).
2026-10-12 | 2026-10-13 | 2026-10-14 | 2026-10-15 | 2026-10-16 | 2026-10-17 | 2026-10-18 |  | WEEKLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-009 Artifitial Ventilation |  |  |  | MONTHLY
PM-003 SCADA strings control. | [7 empty] | QUARTERLY
2026-10-19 | 2026-10-20 | 2026-10-21 | 2026-10-22 | 2026-10-23 | 2026-10-24 | 2026-10-25 |  | BI-ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM-016 Monthly Inspection of Generator Auxliliary. | PM-009 Artifitial Ventilation |  |  |  | ANNUAL
PM-003 SCADA strings control. |  |  | PM-025 Monthly Inspection of O&M building and Internal roads. | PM-016 Bi-Monthly check of Generator (Fortight). |  |  |  | PUBLIC HOLIDAY
2026-10-26 | 2026-10-27 | 2026-10-28 | 2026-10-29 | 2026-10-30 | 2026-10-31 | 2026-11-01 |  | BI-MONTHLY
PM 013 - Weekly Inspection of Weather Stations | PM 006 - Monthly Inspection of Inverters | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-008 Quaterly Inspection of 22kV Power Transformer Dry,
| PM 004 - Monthly Inspection of CC Cabinet. Done |  |  | PM-009 Quaterly inspection of Artifitial Ventilation
PM-003 SCADA strings control. | PM 014 - Monthly Inspection of Energy Meter
2026-11-02 | 2026-11-03 | Notes:
2026 | November
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-10-26 | 2026-10-27 | 2026-10-28 | 2026-10-29 | 2026-10-30 | 2026-10-31 | 2026-11-01
2026-11-02 | 2026-11-03 | 2026-11-04 | 2026-11-05 | 2026-11-06 | 2026-11-07 | 2026-11-08
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-003 Quaterly Visual inspection of Combiner box structure. | MP-017 Biannually Maintenance of CCTV System. | PM-009 Artifitial Ventilation |  |  | LEGEND
PM-003 SCADA strings control. | PM-020 Monthly Inspection of Substation. | PM-003 Biannually Inspection for Combiner box. | PM 005 - Quaterly Visual Inspection of Trackers. | PM-016 Bi-Monthly check of Generator (Fortight).
|  | PM-001Annually Test in Laboratory. |  |  |  |  | WEEKLY
2026-11-09 | 2026-11-10 | 2026-11-11 | 2026-11-12 | 2026-11-13 | 2026-11-14 | 2026-11-15 | MONTHLY
PM 013 - Quaterly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM-001 Annualy IV Curve test |  | PM-009 Artifitial Ventilation |  |  | QUARTERLY
PM-003 SCADA strings control. | PM-001 Biannualy inspectiom to PV Modules | [5 empty] | BI-ANNUAL
2026-11-16 | 2026-11-17 | 2026-11-18 | 2026-11-19 | 2026-11-20 | 2026-11-21 | 2026-11-22 | ANNUAL
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-009 Artifitial Ventilation |  |  | PUBLIC HOLIDAY
PM 012 - Quaterly Inspection of SCADA System done |  |  |  | PM-016 Bi-Monthly check of Generator (Fortight). |  |  | BI-MONTHLY
2026-11-23 | 2026-11-24 | 2026-11-25 | 2026-11-26 | 2026-11-27 | 2026-11-28 | 2026-11-29
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | PM 005 - Quaterly Visual Inspection of Trackers. | PM 006 - Quaterly Inspection of Inverters | PM-008 Monthly Inspection of 22kV Power Transformer Dry,
PM-003 SCADA strings control. |  |  | PM 014 - Quaterly Inspection of Energy Meter | PM-009 Artifitial Ventilation
PM 004 - Quaterly Inspection of CC Cabinet. Done
2026-11-30 | 2026-12-01 | Notes:
2026 | December
MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | SUNDAY
2026-11-30 | 2026-12-01 | 2026-12-02 | 2026-12-03 | 2026-12-04 | 2026-12-05 | 2026-12-06
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | Complete Outstanding PM's and reports | PM-009 Artifitial Ventilation
PM-003 SCADA strings control. | Fire Extinguishers Maintenance
2026-12-07 | 2026-12-08 | 2026-12-09 | 2026-12-10 | 2026-12-11 | 2026-12-12 | 2026-12-13
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Complete Outstanding PM's and reports | PM-016 Bi-Monthly check of Generator (Fortight). | PM-009 Artifitial Ventilation
PM-003 SCADA strings control. | PM-020 Monthly Inspection of Substation. | [5 empty] | LEGEND
2026-12-14 | 2026-12-15 | 2026-12-16 | 2026-12-17 | 2026-12-18 | 2026-12-19 | 2026-12-20
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. | Public holiday | PM 014 - Monthly Inspection of Energy Meter | PM-009 Artifitial Ventilation |  |  | WEEKLY
PM-003 SCADA strings control. | PM 006 - Monthly Inspection of Inverters |  | PM-008 Monthly Inspection of 22kV Power Transformer Dry, | PM 004 - Monthly Inspection of CC Cabinet. Done |  |  | MONTHLY
2026-12-21 | 2026-12-22 | 2026-12-23 | 2026-12-24 | 2026-12-25 | 2026-12-26 | 2026-12-27 | QUARTERLY
PM-005 - Weekly SCADA Trackers monitoring. | PM-003 SCADA strings control. | PM-016 Bi-Monthly check of Generator (Fortight). | Complete Outstanding PM's and reports | Public holiday | Public holiday |  | BI-ANNUAL
PM 013 - Weekly Inspection of Weather Stations | [6 empty] | ANNUAL
HOLIDAY
2026-12-28 | 2026-12-29 | 2026-12-30 | 2026-12-31 | 2027-01-01 | 2027-01-02 | 2027-01-03 | BI-MONTHLY
PM 013 - Weekly Inspection of Weather Stations | PM-005 - Weekly SCADA Trackers monitoring. |  |  | Public holiday |  |  | PUBLIC HOLIDAY

## PREVENTATIVE MAINTENANCE
WITKOP PREVENTATIVE MAINTENANCE PLAN 2025
Task No. | System | Equipment | Procedure Code | Title of Procedure | Task Description | No. of Equipment | Unit of measure | Frequency | Total Annual WL | WL Jan 25 | WL Feb 25 | WL Mar 25 | WL Apr 25 | WL May 25 | WL Jun 25 | WL Jul 25 | WL Aug 25 | WL Sep 25 | WL Oct 25 | WL Nov 25 | WL Dec 25
Astronergy CHSM6612P / SOLAR PV MODULES
1 | PV Array | Solar PV Modules | PM-001 | Biannualy Inspection to PV Modules. | 01. Revision Browning and Yellowing effect 02. Revision of possible damage on the surface of the panels. 03. Revision of Shadows on the panels and remove if necessary. 04. Visual revision of junction boxes. 05. Visual check of connectors and cables. 07. Visual check of stability, rigidity and fixing of the panels. | 99 | Trackers | 2 | 198 | 0 |  |  | 33 | 33 | 33 |  |  |  | 33 | 33 | 33
2 | PV Array | Solar PV Modules | PM-001 | Annualy Inspection to PV Modules. | 09. Thermography 10. Open circuit voltage measurement at string level. 11. Check the back sheets of panels for damage, mould, algae and delamination. 12. Visual check for inflammation, bubbling and/or non-uniformity of relief of the back sheet tedlar. | 99 | Trackers | 1 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0
3 | PV Array | Solar PV Modules | PM-001 | Annualy IV Curve test. | 13. IV Curve measurements of a sample of strings (25% where each string should be measured in a different row). | 108 | Combiner Box | 1 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0
4 | PV Array | Solar PV Modules | PM-001 | Annually Test in Laboratory. | 08. Laboratory flash test. | 10 | PV Module | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0
5 | PV Array | Solar PV Modules | PM-001 | Panel Cleaning to PV Modules. | 06. Panel cleaning. | 99 | Trackers | s | 99 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 99 | 0 | 0 | 0
Astronergy CHSM6612P / LOW VOLTAGE POWER LINES (DC and Grounding Network)
6 | 1 PV Array | Solar PV Modules | PM-002 | Biannually Visual inspection of string connections. | 03. Visual check of the MULTI-CONTACTs are in good condition. | 99 | Trackers | 2 | 198 | [5 empty] | 99 |  |  |  | 99
7 | 1 PV Array | Solar PV Modules | PM-002 | Annualy maintenance to cable strings. | 01. Check the condition pipelines and grounding of metal parts (trays). 02. Check the cabling supporting holders are in good condition. 04. Visual inspection of insulation, covering and splices. 05. Inspection of the critical points that appear in the electrical switchboards. 06. Inspection of the splices in the boxes where insulation faults usually occur. 07. Maintenance of the communication wiring. 08. Measurement of grounding resistance. | 99 | Trackers | 1 | 99 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0
Astronergy CHSM6612P / LOW VOLTAGE CHANNELING
8 | 1 PV Array | Low Voltage Channeling | PM-002.1 | Biannualy Channeling inspection. | 01. Metal tray: treating parts affected by corrosion and correct earth connection 02. PVC tray: treating sections that may be in bad state. 03. Tray channelling: inspection to avoid rodents. 03A. Check string cable guide wire is rigid and free of breakages and corrosion. | 99 | Trackers | 2 | 198 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 0
9 | 1 PV Array | Low Voltage Channeling | PM-002.1 | Annualy Channeling inspection. | 04. Buried channelling: verify sealing of tubes. | 99 | Trackers | 1 | 99 | 0 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kuadrotek / SECONDARY ELECTRICAL PANELS (Lever 1 Stream) String combiner box.
10 | 1 PV Array | String combiner box | PM-003 | SCADA strings control. | 20. Weekly Check for open strings (SCADA) | 99 | Tracker | 52 | 5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 PV Array | String combiner box | PM-003 | Quaterly Visual inspection for Combiner box structure. | 01. Checking for proper fastening, impacts, breaks or deformations of the Level 1 box. 05. Visual inspection of terminals, panels and conductors. 06. Visual inspection of pilots signals of fuses. 07. Grounding condition checking. | 99 | Trackers | 4 | 396 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
12 | 1 PV Array | String combiner box | PM-003 | Biannually Inspection for Combiner box. | 03. Check for proper sealing absence of humidity inside the box 04. Visual inspection of the enclosure associated components such as cable protectors, tightening screws, connectors, anchors. 08. Visual check for loose connections. 09. Location of switches and circuit breakers with deficiencies. 10. Check the condition of the surge arresters. 12. Visual check for possible overheating. 18. Circuit-breaker trip check. 19. Check the condition of the thermal magnet circuit-breakers. 21. Thermo graphical analysis of the electrical control panels 22. Electrical control panel voltages check. | 99 | Trackers | 2 | 198 |  |  |  | 33 | 33 | 33 |  |  | 33 | 33 | 33 | 0
13 | 1 PV Array | String combiner box | PM-003 | Annual Maintenance of Combiner box | 02. Electrical panels general clearing. 11. Insulation measurement of bus bars with respect to grounding. 13. Check the door and lock. 14. Check the plays and identify elements in the control panel and the electrical hazard identification plates. 15. Apply the contact cleaner to all the contacts in the switchboard. 16. Retightening of the screws. 17. Retightening of the switchboard's ring terminals. | 99 | Trackers | 1 | 99 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SunEdison AP90 / Tracker AP90
14 | PV Array | Trackers AP90 | PM-005 | Weekly SCADA Trackers monitoring. | 07. Monitor fault conditions. (SCADA). 07A. Check operating angels. (SCADA). | 99 | Trackers | 52 | 5148 | 396 | 396 | 495 | 396 | 396 | 495 | 396 | 495 | 396 | 396 | 495 | 396
15 | PV Array | Trackers AP90 | PM-005 | Quaterly Visual Inspection of Trackers. | 05. Structure torqued connections check. 06. Visually inspect system components for normal operation and alignment. 08. Tracker controller Inspection. 09. Inclinometer Inspection. 10. Anemometer Inspection. 11. Limit Switches Inspection, 12. Screw Jack Inspection and lubrication, 13. Steel Structure. | 99 | Trackers | 4 | 396 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
16 | PV Array | Trackers AP90 | PM-005 | Annual Maintenance of Trackers. | 01. Inspect module array for proper alignment and check a sample of module rail fasteners for proper connection. 02. Test wind slow function by triggering wind sensor. Repeat for snow and flood sensors if installed. 03. Inspect bearing housing assemblies for misalignment due to settling of piers and adjust position if necessary. 04. Inspect all electrical enclosures for cracking, pests and any other damage. | 99 | Trackers | 1 | 99 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0
ABB PVS800-57-0630kW / SOLAR PHOTOVOLTAIC - INVERTER
17 | CT Builing | Inverters PVS800-57-0630kW | PM-006 | Monthly Inspection of Inverters | 01. General inspection of the equipment. 02. Check the condition of cables and terminals. 05. Check the proper condition and operation of the lighting of the building replacing lamps or tubes if necessary. 11. Verify the absence of alarms in the control equipment. | 48 | Inverters | 12 | 576 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
18 | CT Builing | Inverters PVS800-57-0630kW | PM-006 | Quaterly Inspection of Inverters. | 03. Check the proper tightening of screws works and cables. 04. Visual check of connections. 08. Check the correct ventilation of the equipment. 09. Check the proper state of front air grate and rearwards filters. 13. Change batteries, when it's necessary. 14. Checking the grounding of the inverter. 15. Cleaning of inverter room. | 48 | Inverters | 4 | 192 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48
19 | CT Builing | Inverters PVS800-57-0630kW | PM-006 | Annual Maintenance of Inverters. | 06. Check the lack of humidity inside the cabinet. 07. Check the proper anchoring of equipment (upper and lower). 10. Check the environment condition. 12. Thermography: correct the detected hot spots. | 48 | Inverters | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0
Kuadrotek / SECONDARY ELECTRICAL PANELS (Lever 2 Stream) CC Cabinet.
20 | CT Builing | CC Cabinet | PM-004 | Monthly Inspection of CC Cabinet. | 20. Check the control panel lights and indicators. 23. Check the thermal magnetic device (negative, grounding isolation, monitoring and controller of inverter shutdown). 06. Visual inspection of pilots signals of fuses. | 48 | CC Cabinet | 52 | 2496 | 240 | 192 | 192 | 192 | 240 | 192 | 240 | 192 | 240 | 192 | 192 | 192
21 | CT Builing | CC Cabinet | PM-004 | Quaterly Inspection of CC Cabinet. | 01. Checking for proper fastening, impacts, breaks or deformations of the Level 2 box. 05. Visual inspection of terminals, panels and conductors. 07. Grounding condition checking.. | 48 | CC Cabinet | 4 | 192 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 0 | 48
22 | CT Builing | CC Cabinet | PM-004 | Biannually Inspection of CC Cabinet. | 03. Checking for proper sealing, absence of humidity. 04. Visual inspection of the enclosure associated components such as cable protectors, tightening screws, connectors, anchors. 08. Visually check for possible loose connections. 09. Location of switches or circuit-breakers with possible deficiencies. 10. Checking the correct state of voltage dischargers. 12. Checking for possible excessive overheating of the busbar and the wiring. 18. Circuit-breaker trip check. 19. Inspection of the condition of the thermal magnetic circuit-breakers. 21. Thermo graphic analysis of the switchboard and correction of hot spots. 22. Checking the voltages of the switchboard. 24. Energy Meter Verification/Calibration. | 48 | CC Cabinet | 2 | 96 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0
23 | CT Builing | CC Cabinet | PM-004 | Annual Maintenance of CC Cabinet. | 02. Electrical panels general cleaning. 11. Insulation measurement of bus bars with respect to grounding. 13. Check the door and lock. 14. Check the good condition of the plates and identifying elements in the control panel and electrical hazard. identification plates are in good condition 15. Applying contact grease to all the contacts in the switchboard. 16. Re-tighten the panel protection device screws for the switchboard. 17. Re-tighten the panel ring terminals. | 48 | CC Cabinet | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0
PS / POWER TRANSFORMER (Dry)
24 | CT Builing | 22kV Power Transformer Dry. | PM-008 | Weekly Inspection of 22kV Power Transformer Dry, | 01A.Check Temperature 02A.Check Fans. 03A. Check status of SF6 gas on RMU. | 24 | Transformer | 52 | 1248 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
25 | CT Builing | 22kV Power Transformer Dry. | PM-008 | Quaterly Inspection of 22kV Power Transformer Dry. | 01. Check status of optical and acoustic indicators. 02. Check operation load level of measurement equipment. 03. Check ventilation operation. 04. Check winding temperature indicator (if available). 05. Check dielectric stiffness of power transformer. 06. Cleaning of room air filters. Replace if necessary. | 24 | Transformer | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
26 | CT Builing | 22kV Power Transformer Dry. | PM-008 | Annual Maintenance of 22kV Power Transformer Dry, | 07. Check status of current equipment for motor control 08. General review of operation of switchgear. 09. Openining and closing circuit breaker. 10. Opening and closing of switches manoeuvre. 11. Lubrication of the drive if necessary. 12. Inspection of terminal bottles. 13- Check the ground connections of the electrodes. 14. Wetting of ground wells. 15. Terminal and lid cleaning of power transformer. 16. Check Status of power transformer protection. 17. Check sealing of all joints of the power transformer. 18. Check the heating elements functioning of the power transformer. 19. Check air dryer (Replacement of silica gel when its colour is pink) of the power transformer. 20. Verification of electrical circuit breakers (SF6). 21. Verification of the mechanical circuit breakers status and operating of the circuit breaker interlocks. 22. Status and operating of the circuit breaker interlocks 23. Lubrication of circuit breakers. 24. Visual inspection of instrument transformer. 25. Press contact and review of instrument transformer connections. 26. Check condition of insulators and bus bars. 27. Check Status of insulators connections and bus bars. 28. Resistance measurement of ground network of neutral and hardware. 29. Protection relays checking. 30. Check alarm and trip signals of temperature. 31. Auxiliary relays checking. 32. Alarm system checking. 33. General cleaning. | 24 | Transformer | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0
PS / ARTIFICIAL VENTILATION
27 | CT Builing | Artifitial Ventilation | PM-009 | Weekly Inspection of Artifitial Ventilation. | 01. General state supervision. 02. Absence of unwanted noise checking. | 24 | Ventilation | 52 | 1248 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
28 | CT Builing | Artifitial Ventilation | PM-009 | Quarterly Inspection of Artifitial Ventilation. | 03. Exterior cleaning of equipment and components 04. Current measurement in phases. 05. Thermostat control checking and adjusting. 06. Check status of anchoring and vibration. 07. Check the room air filters and replace if is necessary. | 24 | Ventilation | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
PS / MEDIUM VOLTAGE POWER LINES (AC and Grounding Network)
29 | CT Builing | MV Power line and grounding network. | PM-010 | Annual Inspection of MV Power lind and Grounding network. | 01. Check the condition pipelines and grounding of metal parts (trays). 02. Check the holder condition. 03. Check absence of heating's or vibrations 04. General check of grounding lines. 05. Check the contact and pass heating. 06. Measurement of grounding resistance. | 24 | CT Building | 1 | 24 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0
CONTROL AND SYSTEMS / COMMUNICATIONS
30 | SCADA | Communication systems | PM-011 | Monthly Inspection Communication System | 01. General functioning status checking. | 1 | COMMS | 52 | 52 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
31 | SCADA | Communication systems | PM-011 | Quaterly Inspection of Communication System | 02. Checking of external connections. 03. Exterior cleaning | 1 | COMMS | 4 | 4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
CONTROL AND SYSTEMS / SCADA CONTROL
32 | SCADA | SCADA monitoring | PM-012 | Daily monitoring of SCADA | 01. General functioning status checking. | 1 | SCADA | 365 | 365 | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
33 | SCADA | SCADA monitoring | PM-012 | Quaterly Inspection of SCADA System | 02. External connection checking and retightening 03. Exterior cleaning | 1 | SCADA | 4 | 4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
34 | SCADA | SCADA monitoring | PM-012 | Back up of SCADA | 04. Backups (software and data) | 1 | SCADA | s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GEONICA 3000C / CR1000 WEATHER STATION
35 | MDAS | MET Station | PM-013 | Weekly Inspection of MDAS | 01. General cleaning and inspection of all elements and meteorological sensors. 02. Check of dirt condition of the panels. 12. Cleaning irradiance cells and/or pyranometes with damp cloth and deionised water and keep log book. | 4 | MDAS | 52 | 208 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
36 | MDAS | MET Station | PM-013 | Biannual Inspection of MDAS | 03. Weather temperature measurement and comparison with weather station. 04. Inspection of element anchoring and bolt fastenings. 05. Inspection of verticality and anchoring of mast. | 4 | MDAS | 4 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0
37 | MDAS | MET Station | PM-013 | Annual Maintenance of MDAS | 06. Maintenance of earth systems. 07. Maintenance of electrical installation. 08. Review lightning conductor installation. 10. Check the condition of the supports for the sensors. | 4 | MDAS | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0
38 | MDAS | MET Station | PM-013 | Calibration and Check of MDAS | 09. Review and replace desiccant according to manufacturer instructions. 11. Calibration of pyranometer/reference cell (according to manufacturer instructions) at an official institute. | 4 | MDAS | s | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PS-LV_AUX_FV / SECONDARY ELECTRICAL PANELS (Consumption) Energy Meter cabinet.
39 | CT Builing | Energy Meter Cabinet | PM-014 | Monthly Inspection of Energy Meter | 06. Visual inspection of pilots signals of fuses. 20. Checking the panel lights and indicators. | 24 | CT Building | 52 | 1248 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
40 | CT Builing | Energy Meter Cabinet | PM-014 | Quaterly Inspection of Energy Meter | 01. Checking for proper fastening, possible impacts, breaks or deformations. 05. Visual inspection of terminals, panels and conductors. 07. Grounding condition checking. | 24 | CT Building | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
41 | CT Builing | Energy Meter Cabinet | PM-014 | Biannual Inspection of Energy Meter | 03. Checking for proper sealing, absence of humidity. 04. Visual inspection of the enclosure. 08. Visually check for possible loose connections. 09. Location of switches or circuit-breakers with possible deficiencies. 10. Checking the correct state of voltage dischargers. 12. Checking for possible excessive overheating. 18. Circuit-breaker trip check. 19. Inspection of the condition of the thermal magnetic circuit-breakers. 21. Thermographic analysis of the switchboard. 22. Checking the voltages of the switchboard. 23. Energy Meters Calibration. | 24 | CT Building | 2 | 48 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24
42 | CT Builing | Energy Meter Cabinet | PM-014 | Annual Maintenance of Energy Meter. | 02. Electrical panels general clearing 11. Insulation measurement of bus bars with respect to grounding. 13. Check the door and lock. 14. Check the good condition of the plates and identifying elements in the control panel. 15. Applying contact cleaner. 16. Re-tighten the panel protection device screws. 17. Re-tighten the panel ring terminals. | 24 | CT Building | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0
SECURITY SYSTEM / MANUAL FIRE ALARM SYSTEM
43 | General | Security System & Fire Alarm | PM-015 | Quaterly Inspection to Security and fire alarm systems. | 01. Condition checking of emergency battery. 02. Performance checking of alarm devices. 08. Check location, accessibility and visibility of fire extinguishers. | 24 | CT Building | 4 | 96 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 24
44 | General | Security System & Fire Alarm | PM-015 | Test Check for Security and Fire alarm systems. | 03. Inspection of operation of installations (with each power source). Each 4 months. | 24 | CT Building | 3 | 72 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24
45 | General | Safety System & Fire Alarm | PM-015 | Annual Maintenance of Security and fire alarm systems. | 04. Checking of the overall performance of the installation 05. Cleaning of the components 06. Manual extinguishers revision: - Check the place they are located, accessibility and visibility - Check the correct status of the seals and that they have not been used - External aspect: Absence of corrosion and impacts) - Check the proper pressure indication on the manometer 07. Final test setup (with each power source). | 24 | CT Building | 1 | 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0
GENERATOR / POWER GENERATOR
46 | General | Power Generator | PM-016 | Monthly Inspection of Generator Auxliliary. | 01. General status checking. | 1 | Generator | 12 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
47 | General | Power Generator | PM-016 | Bi-Monthly check of Generator (Fortight). | 02. Start-up batteries connection checking. 03. Grease pump operation checking. 04. Checking of oil, air and fuel levels. 05. Network failure simulation. 06. Checking of automatic start-up of power generator. 07. Checking of automatic performance of network switches and power generator. 08. Checking of power generator's automatic stop. | 1 | Generator | 6 | 6 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1
48 | General | Power Generator | PM-016 | Biannually Inspection of Generator. | 09. Exterior cleaning 10. Brushes and collectors cleaning and condition checking 11. Engine protection alarms checking 12.Unwanted noise and vibration checking | 1 | Generator | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
49 | General | Power Generator | PM-016 | Anual Maintenance of Generator. | 13. Replacement of alternator engine oil (three years). 14. Replacement oil, air and fuel filters (500 hours or 30 months). 15. Replacement of start-up batteries (3 years). | 1 | Generator | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Security System / CCTV.
50 | General | Security System CCTV | PM-017 | Biannually Maintenance of CCTV System. | 01. Checking of all local functions of the Commander, (UP, DOWN, ZOOM, FOCUS), as well as the bumpers of petitioners 02. Check the definition and signal levels from the camera 03. Checking of all feeding stabilised power sources (Amplification systems, camera tensions, systems) 04. Observation of status indicators for the electronic centre 05. General testing of electronic centre system, adjusting timers. 06. Checking of voltage at terminals connected to the detectors of the electronic centre. 07. Checking of performance indicators and testing of expansion PV modules 08. Checking the state and correct functioning of the microwave/infrared barriers 09. Checking the voltage and level of charge of the central control unit batteries. | 45 | Cameras | 1 | 45 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0
51 | General | Security System CCTV | PM-017 | Annually Inspection of CCTV System. | 10. Checking the value of the supply voltage for all the equipment and elements that make up the security installation. 11. Checking the condition of the supports, towers or columns. | 45 | Cameras | 2 | 90 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FENCES / HARDWARE (Perimeter Fence and Accesses)
52 | General | Perimeter Fence | PM-018 | Inspection of the Perimeter Fence. - Each 4 months. | 08. Maintenance of good condition of water drainage system, cleaning and civil maintenance works. 09. Inspect all manholes to ensure that they are intact and that excessive sand or water is not entering them. | 45 | Cameras | 3 | 135 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 45
53 | General | Perimeter Fence | PM-018 | Biannual Maintenance of Perimeter Fence. | 01. Status checking of perimeter fence. 02. Status checking of access gates. 03. Functioning status of latches and hinges 04. Lubrication of gates. 05. Checking of fence corrosion status, proceeding to paint if necessary. 06. Status checking of vegetation, removing if necessary. 07. Apply herbicides in areas of fencing. 10. Maintenance of good condition in internal and access roads. | 45 | Cameras | 2 | 90 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 45 | 0
CIVIL WORKS / CLEARING AND PEST CONTROL
54 | General | All Site | PM-019 | Monthly Visual Inspection Clearing and Pest Control. | 01. General status checking. 05. Visual inspection of inverters buildings for signs of rodents. | 24 | CT Building | 12 | 288 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
55 | General | All Site | PM-019 | Pest Control Application. | 04. Treatment of pest control. Each 4 months. | 24 | CT Building | 3 | 72 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0
56 | General | All Site | PM-019 | Biannually Chemical Control | 02. Chemical weed control / Physical removal as appropriate / grass-cutting. 03. Clearing of small plants that have withstood the chemical treatment. | 99 | CT Building | 2 | 198 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0
SUBSTATION / SUBSTATION - CONTROL BUILDING
57 | Substation | Substation | PM-020 | Monthly Inspection of Substation. | 01.Check Feeder one B/B 132kv Isolator if the links are Closed and locked in all phases 02.Check Feeder One 132kv CT's if Rph,Wph,Bph oil level is correct 03.Check TRFR One 132Kv Breaker is Closed,SF6-Gas Normal and the Counter 04.Check TRFR One 132Kv CT's if Rph,Wph,Bph oil level is correct 05.TRFR One 132Kv Isolator if the links are Closed and locked in all phases,Earth link open B/B side, Earth link open TRFR side 06.TRFR One 132Kv VT's if Rph,Wph,Bph oil level is correct and all CB's Switched on. 07.Transfomer 1 & 2 -Check if main oil level is correct -Check if bucholtz Not Operated -Check if the explosion device not operated -Check if HV surge Arrestors are in order -Check if MV Surge Arrestor are in order -Check oil temperature -Check winding Temperature -Check Ambient Temperature -Check if kiosk is on -Check if Heater is on -Check if silica Gel not coloured -Check if oil level is Correct -Check if main oil level is correct -Check tap changer -Check if the heater is on -Check if the light is on -Check tap changer -Check silica Gel not Coloured -Check earth counter 08. Transformer 1&2 NEC/NER -Check if main oil level is correct -Check if bucholtz Not Operated -Check if the explosion device not operated -Check oil temperature -Check winding Temperature -Check silica Gel not Coloured -Check 22kv Cable in Good condition | 2 | Trasnformer | 12 | 24 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
37 | Substation | Substation | PM-020 | Mantenimiento del Sistema de Iluminacion | Mantenimiento del Sistema de Iluminacion cambiando luces en mal estado. | 1 | Unidad | 1 | 1 | [7 empty] | 1
58 | Substation | Substation | PM-020 | Major Maintenance of Substation. | 01. Cleaning of control panel. 02. Review of operation of signal lamps on the control panel. 03. Function Testing relay of control panel. 04. Test cuts from the relay control panel. 05. Checking of the operation of electromechanical relays on the control panel 06. Review and tighten of terminals at the control panel 07. Manoeuvres making with control panel remote controls 08. Review of operation of automatic and differential Auxiliary Service 09. Review of operation of the remote control and lamp signalling on control panel and auxiliary services 10. Review and tighten the terminals of the Auxiliary Service 11. Review DC battery 12. Check of the high-voltage safety 13. Fire protection material testing 14. Regular lighting testing 15. Emergency lighting testing | 1 | Substation | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
SUBSTATION / SUBSTATION - SUBSTATION CELLS
59 | Substation | Substation Cells | PM-021 | Biannually Inspection of Substation Cells. | 01. Envelope status check 02. Inspection and if necessary retightening of bolts 03. Checking the state of bus bars 04. Interior Cleaning of the cell, bus bars and insulators 05. Cable and terminal bottles checking 06. Check operation of heating element 07. Checking of fuses, auxiliary relays and signal lamp 08. Checking the status of mechanical interlocks 09. Review of mechanical interlocking of cells 10. Joint manoeuvring of the interlocking 11. Checking of manoeuvre signalling on control panel 12. Checking of power cut mechanism 13. General cleaning and lubrication of moving parts | 2 | Transformer | 2 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
SUBSTATION / SUBSTATION - AUXILIARY SERVICE POWER TRANSFORMER
60 | Substation | AASS Power Transformer | PM-023 | Annual Maintenance of Auxiliary Power Transformers. | 01. Check general condition. 02. Inspection and if necessary retightening of bolts. 03. Check operation of temperature sensors. 04. Current measurements in high and low voltage. 05. Checking the state of the cables and terminal bottles.. 06. Ground resistance measurement. 07. Inspection and tightening if necessary of terminal. 08. Measurement of dielectric strength of oil (every 5 years). 09. General Cleaning (see 10.1.1 and (see 10.1.2)). 10. Control encapsulated insulation (see 10.1.7). 11. Control the value of compression of supports (see 10.1.8). 12. Humidity, thermo resistance and functionality control (see 10.1.4, 10.1.5, 10.1.6). 13. General cleaning and lubrication of moving parts. | 2 | Transformer | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
SUBSTATION / SUBSTATION - MV/HV POWER TRANSFORMER
61 | Substation | MV-HV Power Transformer | PM-024 | Major Maintenance of MV-HV Transformers. | 01. Check general condition. 02. Inspection and if necessary retightening of bolts. 03. Check operation of temperature sensors. 04. Current measurements in high and low voltage. 05. Checking the state of the cables and terminal bottles. 06. Ground resistance measurement. 07. Inspection and tightening if necessary of terminals. 08. Measurement of dielectric strength of oil (every 5 years). 09. General Cleaning. 10. Control encapsulated insulation. 11. Control the value of compression of supports. 12. Humidity, thermoresistence and functionality control. | 2 | Transformer | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
O&M Building and Facilities
62 | O&M Facilities | Buildings and Internal roads | PM-025 | Monthly Inspection of O&M building and Internal roads. | 01. Check general condition of O&M buildings 02. Inspection and if necessary repair any defects 03. Check condition of internal roads 04. Inspect storage areas | 1 | Facilities | 12 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1