## Substation
Preventive Maintenance Check List
| Procedure / rev: |  |  |  | Title:
PM-020 |  |  |  |  | Monthly Inspection for Substation
| Made by: |  |  |  | Approved by: |  |  | Date of last revision:
{checklist_made_by} |  |  |  |  | {last_revision_approved_by} |  |  | {last_revision_date}
| Plant: | Witkop Solar Plant |  | Maintenance team: |  | {maintenance_team}
| Date: | {inspection_date} |  | Start hour: | {started_at} |  | Finished hour: |  | {finished_at}
* Note: Perform this inspection with PPE CAT II, dielectric shoes, helmet CAT E and safety glasses.
Inspection complete: YES NO
| # | Description | [6 empty] | Pass | Fail | Remarks
| 1 | Switchyard Inspection
| 1.1 | Check Feeder one B/B 132kv Isolator if the links are Closed and locked in all phases | [8 empty] | {observations}
| 1.2 | Check Feeder One 132kv CT's if Rph,Wph,Bph oil level is correct | [8 empty] | {observations}
| 1.3 | Check TRFR One 132Kv Breaker is Closed,SF6-Gas Normal and the Counter | [8 empty] | {observations}
| 1.4 | Check TRFR One 132Kv CT's if Rph,Wph,Bph oil level is correct | [8 empty] | {observations}
| 1.5 | TRFR One 132Kv Isolator if links are Closed and locked in all phases, Earth link open B/B side, Earth link open TRFR side | [8 empty] | {observations}
| 1.6 | TRFR One 132Kv VT's if Rph,Wph,Bph oil level is correct and all CB's Switched on. | [8 empty] | {observations}
| 2 | Transformer # 1 - 20 MVA 132/22 kV
| 2.1 | Check if main oil level is correct | [8 empty] | {observations}
| 2.2 | Check if bucholtz Not Operated | [8 empty] | {observations}
| 2.3 | Check if the explosion device not operated | [8 empty] | {observations}
| 2.4 | Check if HV surge Arrestors are in order | [8 empty] | {observations}
| 2.5 | Check if MV Surge Arrestor are in order | [8 empty] | {observations}
| 2.6 | Check oil temperature | [8 empty] | {observations}
| 2.7 | Check winding Temperature | [8 empty] | {observations}
| 2.8 | Check Ambient Temperature | [8 empty] | {observations}
| 2.9 | Check if kiosk is on | [8 empty] | {observations}
| 2.1 | Check if Heater is on | [8 empty] | {observations}
| 2.11 | Check if silica Gel not coloured | [8 empty] | {observations}
¿ | 2.12 | Check if oil level is Correct | [8 empty] | {observations}
| 2.13 | Check if main oil level is correct | [8 empty] | {observations}
| 2.14 | Check tap changer | [8 empty] | {observations}
| 2.15 | Check if the heater is on | [8 empty] | {observations}
| 2.16 | Check earth counter | [8 empty] | {observations}
| 3 | Transformer # 2 - 20 MVA 132/22 kV
| 3.1 | Check if main oil level is correct | [8 empty] | {observations}
| 3.2 | Check if bucholtz Not Operated | [8 empty] | {observations}
| 3.3 | Check if the explosion device not operated | [8 empty] | {observations}
| 3.4 | Check if HV surge Arrestors are in order | [8 empty] | {observations}
| 3.5 | Check if MV Surge Arrestor are in order | [8 empty] | {observations}
| 3.6 | Check oil temperature | [8 empty] | {observations}
| 3.7 | Check winding Temperature | [8 empty] | {observations}
| 3.8 | Check Ambient Temperature | [8 empty] | {observations}
| 3.9 | Check if kiosk is on | [8 empty] | {observations}
| 3.1 | Check if Heater is on | [8 empty] | {observations}
| 3.11 | Check if silica Gel not coloured | [8 empty] | {observations}
¿ | 3.12 | Check if oil level is Correct | [8 empty] | {observations}
| 3.13 | Check if main oil level is correct | [8 empty] | {observations}
| 3.14 | Check tap changer | [8 empty] | {observations}
| 3.15 | Check if the heater is on | [8 empty] | {observations}
| 3.16 | Check earth counter | [8 empty] | {observations}
| 4 | Transformer #1 100 KVA 23kV/0.35kV NEC/NER
| 4.1 | Check if main oil level is correct | [8 empty] | {observations}
| 4.2 | Check if bucholtz Not Operated | [8 empty] | {observations}
| 4.3 | Check if the explosion device not operated | [8 empty] | {observations}
| 4.4 | Check if the explosion device not operated | [8 empty] | {observations}
| 4.5 | Check oil temperature and record | [8 empty] | {observations}
| 4.6 | Check winding Temperature and record | [8 empty] | {observations}
| 4.7 | Check silica Gel not Coloured | [8 empty] | {observations}
| 4.8 | Check 22kv Cable in Good condition | [8 empty] | {observations}
| 5 | Transformer #2 100 KVA 23kV/0.35kV NEC/NER
| 5.1 | Check if main oil level is correct | [8 empty] | {observations}
| 5.2 | Check if bucholtz Not Operated | [8 empty] | {observations}
| 5.3 | Check if the explosion device not operated | [8 empty] | {observations}
| 5.4 | Check if the explosion device not operated | [8 empty] | {observations}
| 5.5 | Check oil temperature | [8 empty] | {observations}
| 5.6 | Check winding Temperature | [8 empty] | {observations}
| 5.7 | Check silica Gel not Coloured | [8 empty] | {observations}
| 5.8 | Check 22kv Cable in Good condition | [8 empty] | {observations}
| 6 | Control House
| 6.1 | Is Electrical room clean. Clean if is necessary. | [8 empty] | {observations}
| 6.2 | SCADA cabinet status. Verify system working fine. | [8 empty] | {observations}
| 6.3 | CCTV System cabinet status. Verify the system working fine. | [8 empty] | {observations}
| 6.4 | Battery room clean and bateries status is OK. | [8 empty] | {observations}
| 6.5 | Air Condition in good condition and working | [8 empty] | {observations}
| 6.6 | Ligths working fine. | [8 empty] | {observations}
| 6.7 | Verify trips and start leds on MV and HV relays | [8 empty] | {observations}
| 6.8 | Equipments and PPE for MV & HV maneuvers in good condition and certification up to date. | [8 empty] | {observations}
| 6.9 | battery and AID patches in good condition | [8 empty] | {observations}
| 6.1 | Toilet room is clean. | [8 empty] | {observations}
| 6.11 | Access record to the substation up to date and with enough space. | [8 empty] | {observations}
| 6.12 | After inspection the Substation is locked with a padlock. | [8 empty] | {observations}
| 6.13 | Verify the status of the Fence for Substation. | [8 empty] | {observations}
REMARKS
{final_observations}
|  |  | {inspected_by} | [6 empty] | {approved_by}
| Inspection by (Name & Sign) | [6 empty] | Approve (Name & Sign)
A hard copy is uncontrolled and may be out of date unless it bears a "Controlled Copy" stamp. | [11 empty] | Electronically Controlled Information. Last review on Sharepoint.
PM-020-Monthly Inspection for Substation" - Check List
Pág. 1 de 1