WEATHER STATION

PROCEDURE: PM 013

| PLANT | WITKOP SOLAR PLANT |  | MAINTENANCE TEAM |  |
| --- | --- | --- | --- | --- |
| DATE | 08/01/2025 |  |  | Lerato |
| TIME |  |  |  | Prince |
| LOCATION | CT 15 |  |  | Itumeleng |

| # | DESCRIPTION | Pass | Fail | OBSERVATIONS |
| --- | --- | --- | --- | --- |
| 1 | PYRANOMETER INSPCTION IN POA (PLANE OF ARRAY) |  |  |  |
| 1.1 | Check that the pyranometer is clamped on its base | P |  |  |
| 1.2 | Check for damage, corrosion, encapsulation, decolouration, broken glass | P |  |  |
| 1.3 | Check the system if it’s under shading – Any shading in the system | P |  |  |
| 1.4 | Check that the connections are not poor or if a damaged cable is found | P |  |  |
| 1.5 | With a fibre cloth and demineralised water, clean the glass and dry without leaving dirt | P |  |  |
| 1.6 | Check the connections are completely dry and well secured | P |  |  |
| 1.7 | Check good measure of equipment before and after inspection confirming SCADA values (w/m2) | P |  | Before: 553 After: 555 |
| 2 | CELL REFERENCE INSPECTION IN POA |  |  |  |
| 2.1 | Check that the cell is clamped on its base | P |  |  |
| 2.2 | Check for damage, corrosion, encapsulation, decolouration, broken glass | P |  |  |
| 2.3 | Check the system if it’s under shading – Any shading in the system | P |  |  |
| 2.4 | Check that the connections are not poor or if a damaged cable is found | P |  |  |
| 2.5 | With a fibre cloth and demineralised water, clean the glass and dry without leaving dirt | P |  |  |
| 2.6 | Check the connections are completely dry and well secured | P |  |  |
| 2.7 | Check good measure of equipment before and after inspection confirming SCADA values (w/m2) | P |  | Before:551 After: 553 |
| 3 | PYRANOMETER INSPCTION IN HORIZONTAL PLANE |  |  |  |
| 3.1 | Check that the pyranometer is clamped on its base | P |  |  |
| 3.2 | Check for damage, corrosion, encapsulation, decolouration, broken glass | P |  |  |
| 3.3 | Check the system if it’s under shading – Any shading in the system | P |  |  |
| 3.4 | Check that the connections are not poor or if a damaged cable is found | P |  |  |
| 3.5 | With a fibre cloth and demineralised water, clean the glass and dry without leaving dirt | P |  |  |
| 3.6 | Check the connections are completely dry and well secured | P |  |  |
| 3.7 | Check the correct alignment of the level bubble | P |  |  |
| 3.8 | Check good measure of equipment before and after inspection confirming SCADA values (w/m2) | P |  | Before: 553 After: 554 |
| 4 | GENERAL INSPECTION OF STRUCTURE AND DEVICES |  |  |  |
| 4.1 | Check the external status of Temperature sensor and check the SCADA values (oC) with operator | P |  | SCADA Value: 26.4 |
| 4.2 | Check the external status of Wind sensor and check the SCADA values (m/s) with operator | P |  | SCADA Value: 1.3 |
| 4.3 | Check the status of LANTRONIX, LEDs on OK and equipment communicating | P |  |  |
| 4.4 | With a fibre cloth and demineralised water, clean the backup panel and dry without leaving dirt | P |  |  |
| 4.5 | Check the external status from the battery backup of the system | P |  |  |
| 4.6 | Check the tightness of the control cabinet | P |  |  |
| 4.7 | Verify that the structure is in good condition (free of corrosion, correct fastening) | P |  |  |
| 4.8 | Rain gauge secured and clean | P |  |  |
| 4.9 | Verify that earth wire and spike in good condition (free of corrosion, correct fastening) | P |  |  |

OBSERVATIONS

___________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

INSPECTED BY:                                                                                                      APPROVED BY:

NAME:___Prince_________________________                         NAME:__Floridas________________

SIGNATURE:_______________________                        SIGNATURE:_______________________

INSPECTION COMPLETE: YES         NO