## NSWIT-PM-021-SHT1-r00
Preventive Maintenance Check List
| Procedure / rev: |  |  | Title:
NSPSWIT-SUBST01_BTU_PM-021-r00 |  |  |  | Monthly Inspection for Substation BTU
| Made by: |  |  | Approved by: |  | Date of last revision:
Katlego Mogashoa |  |  |  | Tony Skosana |  | 2021-02-02
| Plant: | Witkop | Crew members:
| Date of control: |  | Start hour: |  | Finished hour: |  |  |  | Maximo WO:
* Note: Perform this inspection with PPE CAT II, dielectric shoes, helmet CAT E and safety glasses.
Inspection complete: YES NO
| # | Description |  |  |  |  | BTU01 Pass/Fail | BTU02 Pass/Fail | Remarks
| 1.1 | Battery Tripping Unit Inspection Checklist
| 1.1.1 | Ambient temperature and ventilation system status
| 1.1.2 | Verify all battery monitoring equipment is operating correctly
| 1.1.3 | Check the float voltage, BST , and other configurable settings, using the front panel controls or meters
| 1.1.4 | Charger output volts
| 1.1.5 | Charger output currents
| 1.2 | Inspect Battery Charger
| 1.2.1 | Ensure that a generous supply of cool, dry air is free to circulate through the charger
| 1.2.2 | Clean the equipment. Dust and dirt impeded heat dissipation. Blow out the charger with low-pressure dry air to remove accumulated dust, dirt and any other contaminants
| 1.2.3 | Check that all connctions are clean and tight. Discolaration of terminals or wires is an indication of loose or corroded connections
| 2 | Check Physical Condition of Batteries |  |  |  |  | BTU01 Pass/Fail | BTU02 Pass/Fail | Remarks
| 2.1 | Structural Integrity of Battery Rack of Cabinet
| 2.2 | General apperance and cleaness of the Batteries, Rack or Cabinet, and Battery Area
| 2.3 | Check for evidence of corrosion at terminals, connections, rack or cabinets
| 2.4 | Clean cell containers: wipe the outside of the cells as necessary with a cloth moistened with water to remove dust and ordinary dirt
| 2.5 | Cell condition; Review manufacturer recommendations
| 2.6 | Cracks in cells or evidence of electrolyte leakage
| 2.7 | Check for unintentinal battery grounds
| 2.8 | Verify the exhaust fan is operational and in good condition
| 3 | Battery Charger Readings |  |  |  |  | BTU01 Pass/Fail | BTU02 Pass/Fail | Remarks
| 3.1 | For the following steps ensure that cells are in float chargecondition. Batteries are fully charged
| 3.2 | Check and record voltage of each cell as per SHT2
| 4 | Connection Integrity - bi-annually |  |  |  |  | BTU01 Pass/Fail | BTU02 Pass/Fail | Remarks
| 4.1 | Re-torque all battery connections as required reference the table in the procedure
| 4.2 | Check connection resistance by measuring resistance post to post (positive post of one cell to the negative post of the next cell) Record these values
| 4.3 | Checking the state of bus bars
| 4.4 | Interior Cleaning of the cell, bus bars and insulators
| 4.5 | Check operation of heating element
| 4.6 | Checking of fuses, auxiliary relays and signal lamp
| 4.7 | Checking the status of mechanical interlocks if applicable
| 4.8 | Review of mechanical interlocking of cells if necessary
| 4.9 | Joint manoeuvring of the interlocking
| 4.1 | Checking of manoeuvre signalling on control panel
| 4.11 | Checking of power cut mechanism
| 4.12 | General cleaning and lubrication of moving parts if any
REMARKS
| Inspection by (Name & Sign) |  |  |  |  | Approve (Name & Sign)
Novasource Power Services Proprietary Information
A hard copy is uncontrolled and may be out of date unless it bears a "Controlled Copy" stamp. | [9 empty] | Electronically Controlled Information. Last review on Sharepoint.
NSPSWIT-SUBST01_BTU_PM-021-r00-Monthly Inspection for Substation BTU" - Check List
Pág. 1 de 1

## NSWIT-PM-021-SHT2-r00
Preventive Maintenance Check List
| Procedure / rev: |  |  |  |  | Title:
PM-021-r00 | [5 empty] | Monthly Inspection for Substation BTU
| Made by: |  |  |  | Approved by: |  |  | Date of last revision:
Neo Chauke |  |  |  |  | Floridas |  |  | 2023-07-04
| Plant: | Witkop Solar Plant |  | Crew members: |  | RABELANI & PRINCE
| Date of control: |  | 04/092023 | Start hour: |  |  | Finished hour:
* Note: Perform this inspection with PPE CAT II, dielectric shoes, helmet CAT E and safety glasses.
Inspection complete: YES NO
| Battery Bank 1 | [6 empty] | Battery Bank 2
| No. | Value | No. | Value |  |  |  | No. | Value | No | Value
| Cell 1 | 1.5 | Cell 44 | 1.5 |  |  |  | Cell 1 | 1.5 | Cell 44 | 1.5
| Cell 2 | 1.3 | Cell 45 | 1.4 |  |  |  | Cell 2 | 1.4 | Cell 45 | 1.4
| Cell 3 | 1.5 | Cell 46 | 1.5 |  |  |  | Cell 3 | 1.4 | Cell 46 | 1.5
| Cell 4 | 1.3 | Cell 47 | 1.4 |  |  |  | Cell 4 | 1.3 | Cell 47 | 1.4
| Cell 5 | 1.5 | Cell 48 | 1.4 |  |  |  | Cell 5 | 1.5 | Cell 48 | 1.5
| Cell 6 | 1.3 | Cell 49 | 1.3 |  |  |  | Cell 6 | 1.4 | Cell 49 | 1.4
| Cell 7 | 1.5 | Cell 50 | 1.5 |  |  |  | Cell 7 | 1.5 | Cell 50 | 1.4
| Cell 8 | 1.3 | Cell 51 | 1.4 |  |  |  | Cell 8 | 1.4 | Cell 51 | 1.4
| Cell 9 | 1.4 | Cell 52 | 1.4 |  |  |  | Cell 9 | 1.4 | Cell 52 | 1.5
| Cell 10 | 1.3 | Cell 53 | 1.3 |  |  |  | Cell 10 | 1.3 | Cell 53 | 1.4
| Cell 11 | 1.5 | Cell 54 | 1.5 |  |  |  | Cell 11 | 1.5 | Cell 54 | 1.4
| Cell 12 | 1.3 | Cell 55 | 1.3 |  |  |  | Cell 12 | 1.4 | Cell 55 | 1.4
| Cell 13 | 1.5 | Cell 56 | 1.5 |  |  |  | Cell 13 | 1.4 | Cell 56 | 1.5
| Cell 14 | 1.3 | Cell 57 | 1.3 |  |  |  | Cell 14 | 1.3 | Cell 57 | 1.4
| Cell 15 | 1.4 | Cell 58 | 1.5 |  |  |  | Cell 15 | 1.5 | Cell 58 | 1.4
| Cell 16 | 1.4 | Cell 59 | 1.3 |  |  |  | Cell 16 | 1.4 | Cell 59 | 1.4
| Cell 17 | 1.4 | Cell 60 | 1.5 |  |  |  | Cell 17 | 1.4 | Cell 60 | 1.4
| Cell 18 | 1.3 | Cell 61 | 1.4 |  |  |  | Cell 18 | 1.4 | Cell 61 | 1.3
| Cell 19 | 1.5 | Cell 62 | 1.5 |  |  |  | Cell 19 | 1.5 | Cell 62 | 1.4
| Cell 20 | 1.4 | Cell 63 | 1.3 |  |  |  | Cell 20 | 1.3 | Cell 63 | 1.3
| Cell 21 | 1.4 | Cell 64 | 1.5 |  |  |  | Cell 21 | 1.5 | Cell 64 | 1.5
| Cell 22 | 1.3 | Cell 65 | 1.5 |  |  |  | Cell 22 | 1.3 | Cell 65 | 1.5
| Cell 23 | 1.4 | Cell 66 | 1.4 |  |  |  | Cell 23 | 1.4 | Cell 66 | 1.4
| Cell 24 | 1.3 | Cell 67 | 1.5 |  |  |  | Cell 24 | 1.3 | Cell 67 | 1.5
| Cell 25 | 1.5 | Cell 68 | 1.4 |  |  |  | Cell 25 | 1.5 | Cell 68 | 1.4
| Cell 26 | 1.3 | Cell 69 | 1.4 |  |  |  | Cell 26 | 1.4 | Cell 69 | 1.5
| Cell 27 | 1.5 | Cell 70 | 1.4 |  |  |  | Cell 27 | 1.5 | Cell 70 | 1.4
| Cell 28 | 1.3 | Cell 71 | 1.5 |  |  |  | Cell 28 | 1.4 | Cell 71 | 1.5
| Cell 29 | 1.4 | Cell 72 | 1.4 |  |  |  | Cell 29 | 1.5 | Cell 72 | 1.4
| Cell 30 | 1.3 | Cell 73 | 1.5 |  |  |  | Cell 30 | 1.4 | Cell 73 | 1.4
| Cell 31 | 1.5 | Cell 74 | 1.4 |  |  |  | Cell 31 | 1.5 | Cell 74 | 1.5
| Cell 32 | 1.4 | Cell 75 | 1.5 |  |  |  | Cell 32 | 1.4 | Cell 75 | 1.4
| Cell 33 | 1.5 | Cell 76 | 1.4 |  |  |  | Cell 33 | 1.5 | Cell 76 | 1.4
| Cell 34 | 1.4 | Cell 77 | 1.5 |  |  |  | Cell 34 | 1.4 | Cell 77 | 1.4
| Cell 35 | 1.5 | Cell 78 | 1.4 |  |  |  | Cell 35 | 1.5 | Cell 78 | 1.4
| Cell 36 | 1.3 | Cell 79 | 1.5 |  |  |  | Cell 36 | 1.4 | Cell 79 | 1.5
| Cell 37 | 1.5 | Cell 80 | 1.4 |  |  |  | Cell 37 | 1.5 | Cell 80 | 1.4
| Cell 38 | 1.3 | Cell 81 | 1.5 |  |  |  | Cell 38 | 1.4 | Cell 81 | 1.5
| Cell 39 | 1.5 | Cell 82 | 1.4 |  |  |  | Cell 39 | 1.5 | Cell 82 | 1.4
| Cell 40 | 1.3 | Cell 83 | 1.5 |  |  |  | Cell 40 | 1.4 | Cell 83 | 1.5
| Cell 41 | 1.5 | Cell 84 | 1.4 |  |  |  | Cell 41 | 1.5 | Cell 84 | 1.4
| Cell 42 | 1.3 | Cell 85 | 1.4 |  |  |  | Cell 42 | 1.3 | Cell 85 | 1.4
| Cell 43 | 1.4 | Cell 86 | 1.4 |  |  |  | Cell 43 | 1.4 | Cell 86 | 1.4
1.4
| Total: | 122,31,4 |  |  |  | Total: | _________ | 122 |  | _________
| Boost: | 129.2 |  |  |  | Boost: | _________ | 130.5 |  | _________
REMARKS

## NSWIT-PM-021-SHT3-r00
Preventive Maintenance Check List
| Procedure / rev: |  |  |  |  | Title:
NSPSWIT-SUBST01_BTU_PM-021-r00 | [5 empty] | Biannualy Inspection for Substation BTU SHT 3
| Made by: |  |  |  | Approved by: |  |  | Date of last revision:
Katlego Mogashoa |  |  |  |  | Tony Skosana |  |  | 2021-02-02
| Plant: | Witkop |  | Crew members:
| Date of control: |  |  | Start hour: |  |  | Finished hour: |  |  |  | Maximo WO:
* Note: Perform this inspection with PPE CAT II, dielectric shoes, helmet CAT E and safety glasses.
Inspection complete: YES NO
| Battery Bank 1 | [6 empty] | Battery Bank 2
| # | Post 2 | Micro - Ω | # | Post 2 | Micro - Ω |  | # | Post 2 | Micro - Ω | # | Post 2 | Micro - Ω
| Cell 1 |  |  | Cell 44 |  |  |  | Cell 1 |  |  | Cell 44
| Cell 2 |  |  | Cell 45 |  |  |  | Cell 2 |  |  | Cell 45
| Cell 3 |  |  | Cell 46 |  |  |  | Cell 3 |  |  | Cell 46
| Cell 4 |  |  | Cell 47 |  |  |  | Cell 4 |  |  | Cell 47
| Cell 5 |  |  | Cell 48 |  |  |  | Cell 5 |  |  | Cell 48
| Cell 6 |  |  | Cell 49 |  |  |  | Cell 6 |  |  | Cell 49
| Cell 7 |  |  | Cell 50 |  |  |  | Cell 7 |  |  | Cell 50
| Cell 8 |  |  | Cell 51 |  |  |  | Cell 8 |  |  | Cell 51
| Cell 9 |  |  | Cell 52 |  |  |  | Cell 9 |  |  | Cell 52
| Cell 10 |  |  | Cell 53 |  |  |  | Cell 10 |  |  | Cell 53
| Cell 11 |  |  | Cell 54 |  |  |  | Cell 11 |  |  | Cell 54
| Cell 12 |  |  | Cell 55 |  |  |  | Cell 12 |  |  | Cell 55
| Cell 13 |  |  | Cell 56 |  |  |  | Cell 13 |  |  | Cell 56
| Cell 14 |  |  | Cell 57 |  |  |  | Cell 14 |  |  | Cell 57
| Cell 15 |  |  | Cell 58 |  |  |  | Cell 15 |  |  | Cell 58
| Cell 16 |  |  | Cell 59 |  |  |  | Cell 16 |  |  | Cell 59
| Cell 17 |  |  | Cell 60 |  |  |  | Cell 17 |  |  | Cell 60
| Cell 18 |  |  | Cell 61 |  |  |  | Cell 18 |  |  | Cell 61
| Cell 19 |  |  | Cell 62 |  |  |  | Cell 19 |  |  | Cell 62
| Cell 20 |  |  | Cell 63 |  |  |  | Cell 20 |  |  | Cell 63
| Cell 21 |  |  | Cell 64 |  |  |  | Cell 21 |  |  | Cell 64
| Cell 22 |  |  | Cell 65 |  |  |  | Cell 22 |  |  | Cell 65
| Cell 23 |  |  | Cell 66 |  |  |  | Cell 23 |  |  | Cell 66
| Cell 24 |  |  | Cell 67 |  |  |  | Cell 24 |  |  | Cell 67
| Cell 25 |  |  | Cell 68 |  |  |  | Cell 25 |  |  | Cell 68
| Cell 26 |  |  | Cell 69 |  |  |  | Cell 26 |  |  | Cell 69
| Cell 27 |  |  | Cell 70 |  |  |  | Cell 27 |  |  | Cell 70
| Cell 28 |  |  | Cell 71 |  |  |  | Cell 28 |  |  | Cell 71
| Cell 29 |  |  | Cell 72 |  |  |  | Cell 29 |  |  | Cell 72
| Cell 30 |  |  | Cell 73 |  |  |  | Cell 30 |  |  | Cell 73
| Cell 31 |  |  | Cell 74 |  |  |  | Cell 31 |  |  | Cell 74
| Cell 32 |  |  | Cell 75 |  |  |  | Cell 32 |  |  | Cell 75
| Cell 33 |  |  | Cell 76 |  |  |  | Cell 33 |  |  | Cell 76
| Cell 34 |  |  | Cell 77 |  |  |  | Cell 34 |  |  | Cell 77
| Cell 35 |  |  | Cell 78 |  |  |  | Cell 35 |  |  | Cell 78
| Cell 36 |  |  | Cell 79 |  |  |  | Cell 36 |  |  | Cell 79
| Cell 37 |  |  | Cell 80 |  |  |  | Cell 37 |  |  | Cell 80
| Cell 38 |  |  | Cell 81 |  |  |  | Cell 38 |  |  | Cell 81
| Cell 39 |  |  | Cell 82 |  |  |  | Cell 39 |  |  | Cell 82
| Cell 40 |  |  | Cell 83 |  |  |  | Cell 40 |  |  | Cell 83
| Cell 41 |  |  | Cell 84 |  |  |  | Cell 41 |  |  | Cell 84
| Cell 42 |  |  | Cell 85 |  |  |  | Cell 42 |  |  | Cell 85
| Cell 43 |  |  | Cell 86 |  |  |  | Cell 43 |  |  | Cell 86
REMARKS