WEATHER STATION

PROCEDURE: PM 013

| PLANT | WITKOP SOLAR PLANT |  | MAINTENANCE TEAM | Tumelo |
| --- | --- | --- | --- | --- |
| DATE | 1/5/2026 |  |  |  |
| TIME | 1/5/2026, 3:47:31 PM |  |  |  |
| LOCATION | Main Plant Area |  |  |  |

| # | DESCRIPTION | Pass | Fail | OBSERVATIONS |
| --- | --- | --- | --- | --- |
| 1 | PYRANOMETER INSPCTION IN POA (PLANE OF ARRAY) |  |  |  |
| 1.1 | Check that the pyranometer is clamped on its base | undefined | undefined | All well |
| 1.2 | Check for damage, corrosion, encapsulation, decolouration, broken glass | undefined | undefined | All well |
| 1.3 | Check the system if it’s under shading – Any shading in the system | undefined | undefined | All well |
| 1.4 | Check that the connections are not poor or if a damaged cable is found | undefined | undefined | All well |
| 1.5 | With a fibre cloth and demineralised water, clean the glass and dry without leaving dirt | undefined | undefined | All well |
| 1.6 | Check the connections are completely dry and well secured | undefined | undefined | All well |
| 1.7 | Check good measure of equipment before and after inspection confirming SCADA values (w/m2) | undefined | undefined | Before: undefined After: undefined |
| 2 | CELL REFERENCE INSPECTION IN POA |  |  |  |
| 2.1 | Check that the cell is clamped on its base | undefined | undefined | All well |
| 2.2 | Check for damage, corrosion, encapsulation, decolouration, broken glass | undefined | undefined | All well |
| 2.3 | Check the system if it’s under shading – Any shading in the system | undefined | undefined | All well |
| 2.4 | Check that the connections are not poor or if a damaged cable is found | undefined | undefined | All well |
| 2.5 | With a fibre cloth and demineralised water, clean the glass and dry without leaving dirt | undefined | undefined | All well |
| 2.6 | Check the connections are completely dry and well secured | undefined | undefined | All well |
| 2.7 | Check good measure of equipment before and after inspection confirming SCADA values (w/m2) | undefined | undefined | Before: undefined After: undefined |
| 3 | PYRANOMETER INSPCTION IN HORIZONTAL PLANE |  |  |  |
| 3.1 | Check that the pyranometer is clamped on its base | undefined | undefined | All well |
| 3.2 | Check for damage, corrosion, encapsulation, decolouration, broken glass | undefined | undefined | All well |
| 3.3 | Check the system if it’s under shading – Any shading in the system | undefined | undefined | All well |
| 3.4 | Check that the connections are not poor or if a damaged cable is found | undefined | undefined | All well |
| 3.5 | With a fibre cloth and demineralised water, clean the glass and dry without leaving dirt | undefined | undefined | All well |
| 3.6 | Check the connections are completely dry and well secured | undefined | undefined | All well |
| 3.7 | Check the correct alignment of the level bubble | undefined | undefined | All well |
| 3.8 | Check good measure of equipment before and after inspection confirming SCADA values (w/m2) | undefined | undefined | Before: undefined After: undefined |
| 4 | GENERAL INSPECTION OF STRUCTURE AND DEVICES |  |  |  |
| 4.1 | Check the external status of Temperature sensor and check the SCADA values (oC) with operator | undefined | undefined | SCADA Value: undefined |
| 4.2 | Check the external status of Wind sensor and check the SCADA values (m/s) with operator | undefined | undefined | SCADA Value: undefined |
| 4.3 | Check the status of LANTRONIX, LEDs on OK and equipment communicating | undefined | undefined | All well |
| 4.4 | With a fibre cloth and demineralised water, clean the backup panel and dry without leaving dirt | undefined | undefined | All well |
| 4.5 | Check the external status from the battery backup of the system | undefined | undefined | All well |
| 4.6 | Check the tightness of the control cabinet | undefined | undefined | All well |
| 4.7 | Verify that the structure is in good condition (free of corrosion, correct fastening) | undefined | undefined | All well |
| 4.8 | Rain gauge secured and clean | undefined | undefined | All well |
| 4.9 | Verify that earth wire and spike in good condition (free of corrosion, correct fastening) | undefined | undefined | All well |

OBSERVATIONS

All well

INSPECTED BY:                                                                                                      APPROVED BY:

NAME: ___Prince_____                                       NAME: ________

SIGNATURE: _______________________                        SIGNATURE: _______________________

INSPECTION COMPLETE: YES   {}    NO   {}